## 60228
Stranded Soft Drawn Bare Copper Conductor
(a) Description:-
* Plain bare soft drawn Copper conductors (Circular - Compacted)
(b) Application:-
* Bare stranded soft-drawn (annealed) copper conductor is suitable for uninsulated hook up, jumpers and grounding conductors
in electrical construction, where high conductivity and flexibility are required.
(c) Technical Data:-
| Relevent Standard |  | IEC 60228 class 2
| Conductor |  | Plain bare soft drawn Copper conductors
| Minimum bending Radius |  | 10 x outer diameter
| Packing Condition |  | Our standard length on Wooden Drum / or according to customer request
Product-code | Cross | Minimum Number of Wires | Max. D.C. Conductor | Approx. Overall | Approx.
| Sectional Area |  | Resistance at 20 oC | Diameter | Weight
| mm2 | No. | Ω/km | mm | Kg/km
PR-CT10-00-01-U0 | 10 | 6 | 1.83 | 3.7 | 85
PR-CT11-00-01-U0 | 16 | 6 | 1.15 | 4.7 | 135
PR-CT12-00-01-U0 | 25 | 6 | 0.727 | 5.8 | 215
PR-CT13-00-01-U0 | 35 | 6 | 0.524 | 6.9 | 300
PR-CT14-00-01-U0 | 50 | 6 | 0.387 | 8 | 410
PR-CT15-00-01-U0 | 70 | 12 | 0.268 | 9.75 | 595
PR-CT16-00-01-U0 | 95 | 15 | 0.193 | 11.3 | 820
PR-CT17-00-01-U0 | 120 | 18 | 0.153 | 12.7 | 1030
PR-CT18-00-01-U0 | 150 | 18 | 0.124 | 14 | 1277
PR-CT19-00-01-U0 | 185 | 30 | 0.0991 | 15.9 | 1600
PR-CT20-00-01-U0 | 240 | 34 | 0.0754 | 18.3 | 2100
PR-CT21-00-01-U0 | 300 | 34 | 0.0601 | 20.5 | 2650
PR-CT22-00-01-U0 | 400 | 53 | 0.047 | 23.2 | 3410
PR-CT23-00-01-U0 | 500 | 53 | 0.0366 | 26.5 | 4400
PR-CT24-00-01-U0 | 630 | 53 | 0.0283 | 30.1 | 5600
The above data is approximate and subjected to manufacturing tolerance.

## DIN 48201-1
Stranded Hard Drawn Bare Copper Conductor
(a) Description:-
* Plain bare hard drawn copper conductors (Circular - Non Compacted)
(b) Application:-
* Bare stranded hard-drawn copper conductor is suitable for overhead transmission and distribution networks applications, where the highest electrical conductivity
per unit area and good strength-to-weight ratio are required.
(c) Technical Data:-
| Relevent Standard |  | DIN 48201-1, BS 7884
| Conductor |  | Plain bare hard drawn copper
| Minimum bending Radius |  | 10 x outer diameter
| Packing Condition |  | Our standard length on Wooden Drum / or according to customer request
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Minimum | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
a- DIN 48201-1
PR-HT10-00-01-U0 | 10 | 7 x 1.35 | 1.829 | 4.1 | 4.02 | 90 | 90
PR-HT11-00-01-U0 | 16 | 7 x 1.70 | 1.154 | 5.1 | 6.37 | 143 | 125
PR-HT12-00-01-U0 | 25 | 7 x 2.10 | 0.7563 | 6.3 | 9.72 | 218 | 160
PR-HT13-00-01-U0 | 35 | 7 x 2.50 | 0.5337 | 7.5 | 13.77 | 310 | 200
PR-HT14-00-01-U0 | 50 | 7 x 3.00 | 0.3706 | 9 | 19.84 | 446 | 260
PR-HT14-00-01-U0 | 50 | 19 x 1.80 | 0.3819 | 9 | 19.38 | 437 | 250
PR-HT15-00-01-U0 | 70 | 19 x 2.10 | 0.2806 | 10.5 | 26.38 | 596 | 310
PR-HT16-00-01-U0 | 95 | 19 x 2.50 | 0.198 | 12.5 | 37.39 | 843 | 380
PR-HT17-00-01-U0 | 120 | 19 x 2.80 | 0.1578 | 14 | 46.9 | 1060 | 440
PR-HT18-00-01-U0 | 150 | 37 x 2.25 | 0.1264 | 15.75 | 58.96 | 1337 | 510
PR-HT19-00-01-U0 | 185 | 37 x 2.50 | 0.1024 | 17.5 | 72.81 | 1649 | 589
PR-HT20-00-01-U0 | 240 | 61 x 2.25 | 0.07528 | 20.3 | 97.23 | 2209 | 700
PR-HT21-00-01-U0 | 300 | 61 x 2.50 | 0.06097 | 22.5 | 120.04 | 2725 | 800
PR-HT22-00-01-U0 | 400 | 61 x 2.89 | 0.0456 | 26 | 160.42 | 3640 | 960
PR-HT23-00-01-U0 | 500 | 61 x 3.23 | 0.0365 | 29.1 | 200.38 | 4545 | 1110
PR-HT24-00-01-U0 | 630 | 61 x 3.62 | 0.029 | 32.58 | 251.6903 | 5700 | 1274.4
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec. emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## BS 7884
Stranded Hard Drawn Bare Copper Conductor
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Minimum | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
b - BS 7884
HDC - 10 | 10 | 7 x 1.35 | 1.829 | 4.05 | 3.752 | 89.82 | 90
HDC - 14 | 14 | 7 x 1.60 | 1.303 | 4.8 | 5.267 | 126.2 | 113.4
HDC - 16 | 16 | 7 x 1.70 | 1.154 | 5.1 | 5.946 | 142.4 | 125
HDC - 25 | 25 | 7 x 2.10 | 0.7563 | 6.3 | 9.073 | 217.3 | 160
HDC - 32 | 32 | 7 x 2.46 | 0.5497 | 7.38 | 12.442 | 298.2 | 197.1
HDC - 35 | 35 | 7 x 2.50 | 0.5337 | 7.5 | 12.86 | 308 | 200
HDC - 50 | 50 | 7 x 3.0 | 0.3706 | 9 | 18.52 | 443.5 | 260
HDC - 50 | 50 | 19 x 1.80 | 0.3819 | 9 | 17.7 | 435.8 | 250
HDC - 70 | 70 | 7 x 3.55 | 0.2646 | 10.65 | 25.93 | 621.1 | 314.1
HDC - 70 | 70 | 19 x 2.10 | 0.2806 | 10.5 | 24.09 | 593.2 | 310
HDC - 95 | 95 | 19 x 2.50 | 0.198 | 12.5 | 34.14 | 840.7 | 380
HDC - 100 | 100 | 7 x 4.30 | 0.181 | 12.9 | 36.54 | 911.2 | 400.5
HDC - 120 | 120 | 19 x 2.80 | 0.1578 | 14 | 42.83 | 1055 | 440
HDC - 125 | 125 | 19 x 2.90 | 0.1471 | 14.5 | 45.94 | 1131 | 459
HDC - 150 | 150 | 19 x 3.20 | 0.1208 | 16 | 55.94 | 1377 | 521.1
HDC - 150 | 150 | 37 x 2.25 | 0.1264 | 15.75 | 53.88 | 1334 | 510
HDC - 185 | 185 | 19 x 3.55 | 0.09815 | 17.75 | 68.86 | 1695 | 594.9
HDC - 185 | 185 | 37 x 2.50 | 0.1024 | 17.5 | 66.49 | 1647 | 589
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAC Gremany
All Aluminum Conductors (AAC)
(a) Description:-
* Hard drawn Aluminum wires , stranded in successive layers , in opposite direction to form the Aluminum stranded AAC conductor,
(b) Application:-
* All Aluminum Conductors (AAC) can be used as a bare overhead conductor for distribution lines. Because of its low strength-to-weight ratio,
(AAC) has limited use in transmission lines. AAC is extensively used in urban areas where spans are usually short but high conductivity isrequired.
(c) Technical Data:-
| Relevent Standard |  | BS EN 50182, BS 215-1, DIN 48201-5, IEC 61089, ASTM B 231
| Conductor |  | Plain bare hard drawn Aluminum - H14
| Minimum bending Radius |  | 10 x outer diameter
| Packing Condition |  | Our standard length on Wooden Drum / or according to customer request
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Minimum | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
A - BS EN 50182 (GREMANY) & DIN 48201-5
PO-BT11-00-01-U0 | 16 | 7 x 1.70 | 1.7986 | 5.1 | 3.02 | 43.4 | 110
PO-BT12-00-01-U0 | 25 | 7 x 2.10 | 1.1787 | 6.3 | 4.36 | 66.3 | 145
PO-BT13-00-01-U0 | 35 | 7 x 2.50 | 0.8317 | 7.5 | 6.01 | 93.9 | 180
PO-BT14-00-01-U0 | 50 | 7 x 3.00 | 0.5776 | 9 | 8.41 | 135.2 | 225
PO-BT14-00-01-U0 | 50 | 19 x 1.80 | 0.5944 | 9 | 8.94 | 132.9 | 225
PO-BT15-00-01-U0 | 70 | 19 x 2.10 | 0.4367 | 10.5 | 11.85 | 180.9 | 270
PO-BT16-00-01-U0 | 95 | 19 x 2.50 | 0.3081 | 12.5 | 16.32 | 256.3 | 340
PO-BT17-00-01-U0 | 120 | 19 x 2.80 | 0.2456 | 14 | 19.89 | 321.5 | 390
PO-BT18-00-01-U0 | 150 | 37 x 2.25 | 0.196 | 15.8 | 26.48 | 405.7 | 455
PO-BT19-00-01-U0 | 185 | 37 x 2.50 | 0.1588 | 17.5 | 31.78 | 500.9 | 520
PO-BT20-00-01-U0 | 240 | 61 x 2.25 | 0.1193 | 20.3 | 43.66 | 671.1 | 625
PO-BT21-00-01-U0 | 300 | 61 x 2.50 | 0.0966 | 22.5 | 52.4 | 828.5 | 710
PO-BT22-00-01-U0 | 400 | 61 x 2.89 | 0.0723 | 26 | 68.02 | 1107.1 | 855
PO-BT23-00-01-U0 | 500 | 61 x 3.23 | 0.0579 | 29.1 | 82.47 | 1382.9 | 990
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAC U.K
All Aluminum Conductors (AAC)
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
B - BS EN 50182 (United Kingdom)
MIDGE | 23.3 | 7 x 2.06 | 1.2249 | 6.18 | 4.2 | 63.8 | 139
GNAT | 26.9 | 7 x 2.21 | 1.0643 | 6.63 | 4.83 | 73.4 | 152.7
MOSQUITO | 36.9 | 7 x 2.59 | 0.7749 | 7.77 | 6.27 | 100.8 | 186.8
LADYBIRD | 42.8 | 7 x 2.79 | 0.6678 | 8.37 | 7.28 | 117 | 205
ANT | 52.8 | 7 x 3.1 | 0.5409 | 9.3 | 8.72 | 144.4 | 234
FLY | 63.6 | 7 x 3.4 | 0.4497 | 10.2 | 10.49 | 173.7 | 264
BLUEBOTTLE | 73.6 | 7 x 3.66 | 0.388 | 11 | 11.78 | 201.3 | 290.5
EARWING | 78.6 | 7 x 3.78 | 0.3638 | 11.3 | 12.57 | 214.7 | 302
GRASSHOPPER | 84.1 | 7 x 3.91 | 0.34 | 11.7 | 13.45 | 229.7 | 315
CLEGG | 95.6 | 7 x 4.17 | 0.2989 | 12.5 | 15.3 | 261.3 | 343
WASP | 106 | 7 x 4.39 | 0.2697 | 13.2 | 16.95 | 289.6 | 366
BEETLE | 106.4 | 19 x 2.67 | 0.2701 | 13.4 | 18.08 | 292.4 | 368
BEE | 132 | 7 x 4.90 | 0.2165 | 14.7 | 21.12 | 360.8 | 421
HORNET | 157.6 | 19 x 3.25 | 0.1823 | 16.3 | 26.01 | 433.2 | 473
CATERPILLER | 185.9 | 19 x 3.53 | 0.1546 | 17.7 | 29.75 | 511.1 | 526
CHAFER | 213.2 | 19 x 3.78 | 0.1348 | 18.9 | 34.12 | 586 | 574
SPIDER | 237.6 | 19 x 3.99 | 0.121 | 20 | 38.01 | 652.9 | 615
COCKROACH | 265.7 | 19 x 4.22 | 0.1081 | 21.1 | 42.52 | 730 | 660
BUTTERFLY | 322.7 | 19 x 4.65 | 0.0891 | 23.3 | 51.63 | 886.8 | 748
DRONE | 372.4 | 37 x 3.58 | 0.0774 | 25.1 | 59.59 | 1027.1 | 821
CENTIPEDE | 415.2 | 37 x 3.78 | 0.0695 | 26.5 | 66.43 | 1145.1 | 879
MAYBUG | 486.1 | 37 x 4.09 | 0.0593 | 28.6 | 77.78 | 1340.6 | 972
SCORPION | 529.8 | 37 x 4.27 | 0.0544 | 29.9 | 84.77 | 1461.2 | 1026
CICADA | 628.3 | 37 x 4.65 | 0.0459 | 32.6 | 100.54 | 1732.9 | 1143
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAC IEC
All Aluminum Conductors (AAC)
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
C - IEC 61089
A1 - 16 | 16 | 7 x 1.71 | 1.7896 | 5.12 | 3.04 | 43.8 | 146
A1 - 25 | 25 | 7 x 2.13 | 1.1453 | 6.4 | 4.5 | 68.4 | 194
A1 - 40 | 40 | 7 x 2.70 | 0.7158 | 8.09 | 6.8 | 109.4 | 262
A1 - 63 | 63 | 7 x 3.39 | 0.4545 | 10.2 | 10.39 | 172.3 | 351
A1 - 100 | 100 | 19 x 2.59 | 0.2877 | 12.9 | 17 | 274.8 | 472
A1 - 125 | 125 | 19 x 2.89 | 0.2302 | 14.5 | 21.25 | 343.6 | 545
A1 - 160 | 160 | 19 x 3.27 | 0.1798 | 16.4 | 26.4 | 439.8 | 638
A1 - 200 | 200 | 19 x 3.66 | 0.1439 | 18.3 | 32 | 549.7 | 737
A1 - 250 | 250 | 19 x 4.09 | 0.1151 | 20.5 | 40 | 687.1 | 852
A1 - 315 | 315 | 37 x 3.29 | 0.0916 | 23 | 51.97 | 867.9 | 987
A1 - 400 | 400 | 37 x 3.71 | 0.0721 | 26 | 64 | 1102 | 1152
A1 - 450 | 450 | 37 x 3.94 | 0.0641 | 27.5 | 72 | 1239.8 | 1240
A1 - 500 | 500 | 37 x 4.15 | 0.0577 | 29 | 80 | 1377.6 | 1327
A1 - 560 | 560 | 37 x 4.39 | 0.0515 | 30.7 | 89.6 | 1542.9 | 1425
A1 - 630 | 630 | 61 x 3.63 | 0.0458 | 32.6 | 100.8 | 1738.3 | 1535
A1 - 710 | 710 | 61 x 3.85 | 0.0407 | 34.6 | 113.6 | 1959.1 | 1653
A1 - 800 | 800 | 61 x 4.09 | 0.0361 | 36.8 | 128 | 2207.4 | 1783
A1 - 900 | 900 | 61 x 4.33 | 0.0321 | 39 | 144 | 2483.3 | 1914
A1 - 1000 | 1000 | 61 x 4.57 | 0.0289 | 41 | 160 | 2759.2 | 2039
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 20 °C , final temperature of 80 °C, wind velocity of 1.0 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAC BS 215-1
All Aluminum Conductors (AAC)
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
D - BS 215-1
MIDGE | 22 | 7 x 2.06 | 1.227 | 6.18 | 3.99 | 64 | 139
ANT | 50 | 7 x 3.10 | 0.5419 | 9.3 | 8.28 | 145 | 234
FLY | 60 | 7 x 3.40 | 0.4505 | 10.2 | 9.9 | 174 | 264
WASP | 100 | 7 x 4.39 | 0.2702 | 13.17 | 16 | 290 | 366
HORNET | 150 | 19 x 3.25 | 0.1825 | 16.25 | 25.7 | 434 | 472
CHAFER | 200 | 19 x 3.78 | 0.1349 | 18.9 | 32.4 | 587 | 573
COCKROACH | 250 | 19 x 4.22 | 0.1083 | 21.1 | 40.4 | 731 | 660
BUTTERFLY | 300 | 19 x 4.65 | 0.08916 | 23.25 | 48.75 | 888 | 748
CENTIPEDE | 400 | 37 x 3.78 | 0.06944 | 26.46 | 63.1 | 1145 | 879
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAC ASTM B 231
All Aluminum Conductors (AAC)
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
E - ASTM B 231
PEACHBELL | 13.3 | 7 x 1.56 | 2.1402 | 4.68 | 2.53 | 36.6383 | 98
ROSE | 21.1 | 7 x 1.96 | 1.3558 | 5.88 | 3.91 | 58.2 | 130
IRIS | 33.6 | 7 x 2.47 | 0.8537 | 7.41 | 5.99 | 92.6 | 175
PANSY | 42.4 | 7 x 2.78 | 0.674 | 8.34 | 7.3 | 116.6 | 204
POPPY | 53.5 | 7 x 3.12 | 0.5351 | 9.36 | 8.84 | 147.2 | 236
ASTER | 67.4 | 7 x 3.50 | 0.4252 | 10.5 | 11.1 | 185.7 | 273
PHLOX | 85 | 7 x 3.93 | 0.3373 | 11.79 | 13.5 | 233.9 | 317
OXLIP | 107.2 | 7 x 4.42 | 0.2666 | 13.26 | 17 | 295.2 | 369
VALERIAN | 126.7 | 19 x 2.91 | 0.2277 | 14.55 | 20.7 | 348.6 | 410
SNEEZEWORT | 126.7 | 7 x 4.80 | 0.2261 | 14.4 | 20.1 | 348.8 | 410
LAUREL | 135.2 | 19 x 3.01 | 0.2129 | 15.05 | 22.1 | 372.2 | 428
PEONY | 152 | 19 x 3.19 | 0.1895 | 15.95 | 24.3 | 418.3 | 461
TULIP | 170.5 | 19 x 3.38 | 0.1688 | 16.9 | 27.3 | 469.5 | 497
DAFFODIL | 177.3 | 19 x 3.45 | 0.162 | 17.25 | 28.4 | 487.9 | 510
CANNA | 201.4 | 19 x 3.67 | 0.1432 | 18.35 | 31.6 | 554.9 | 552
GOLDENTUFT | 228 | 19 x 3.91 | 0.1262 | 19.55 | 35 | 627.6 | 599
SYRINGA | 241.7 | 37 x 2.88 | 0.1197 | 20.16 | 38.6 | 664.8 | 620
COSMOS | 241.7 | 19 x 4.02 | 0.1194 | 20.1 | 37 | 664.8 | 620
HYACINTH | 253.3 | 37 x 2.95 | 0.1141 | 20.65 | 40.5 | 696.8 | 640
ZINNIA | 253.3 | 19 x 4.12 | 0.1136 | 20.6 | 38.9 | 697.1 | 640
MISTLETOE | 282 | 37 x 3.12 | 0.102 | 21.84 | 44.3 | 775.7 | 687
DAHLIA | 282 | 19 x 4.35 | 0.1019 | 21.75 | 43.3 | 775.8 | 687
MEADOWSWEET | 304 | 37 x 3.23 | 0.0952 | 22.61 | 47.5 | 836.3 | 718
ORCHID | 322.3 | 37 x 3.33 | 0.0893 | 23.31 | 50.4 | 886.9 | 748
HEUCHERA | 329.4 | 37 x 3.37 | 0.0874 | 23.59 | 51.7 | 907.4 | 759
FLAG | 354.7 | 61 x 2.72 | 0.0815 | 24.48 | 57.1 | 975.8 | 793
VERBENA | 354.7 | 37 x 3.49 | 0.0815 | 24.43 | 55.4 | 975.7 | 793
NASTURTIUM | 362.6 | 61 x 2.75 | 0.0798 | 24.75 | 58.4 | 998.5 | 805
VIOLET | 362.6 | 37 x 3.53 | 0.0797 | 24.71 | 56.7 | 998.5 | 805
CATTAIL | 380 | 61 x 2.82 | 0.0759 | 25.38 | 60.3 | 1046 | 831
PETUNIA | 380 | 37 x 3.62 | 0.0758 | 25.34 | 58.6 | 1046 | 831
LILAC | 402.8 | 61 x 2.90 | 0.0717 | 26.1 | 63.8 | 1110 | 860
ARBUTUS | 402.8 | 37 x 3.72 | 0.0718 | 26.04 | 61.8 | 1109 | 860
SNAPDRAGON | 456 | 61 x 3.09 | 0.0632 | 27.81 | 70.8 | 1256 | 932
COCKSCOMB | 456 | 37 x 3.96 | 0.0633 | 27.72 | 68.4 | 1256 | 932
GOLDENNROD | 483.4 | 61 x 3.18 | 0.0597 | 28.62 | 75 | 1331 | 968
MAGNOLIA | 483.4 | 37 x 4.08 | 0.0597 | 28.56 | 72.6 | 1331 | 968
CAMELLIA | 506.7 | 61 x 3.25 | 0.0571 | 29.25 | 78.3 | 1394 | 996
HAWKWEED | 506.7 | 37 x 4.18 | 0.0569 | 29.26 | 76.2 | 1395 | 996
LARKSPUR | 523.7 | 61 x 3.31 | 0.0551 | 29.79 | 81.3 | 1442 | 1019
BLUEBELL | 523.7 | 37 x 4.25 | 0.055 | 29.75 | 78.8 | 1441 | 1019
MARIGOLD | 564 | 61 x 3.43 | 0.0513 | 30.87 | 87.3 | 1553 | 1066
HAWTHORM | 604.2 | 61 x 3.55 | 0.0479 | 31.95 | 93.5 | 1662 | 1113
NARCISSUS | 644.5 | 61 x 3.67 | 0.0448 | 33.03 | 98.1 | 1774 | 1161
COLUMBINE | 694.8 | 61 x 3.78 | 0.0422 | 34.02 | 104 | 1884 | 1205
CARNATION | 725.1 | 61 x 3.89 | 0.0399 | 35.01 | 108 | 1997 | 1247
GLADIOLUS | 765.4 | 61 x 4.00 | 0.0377 | 36 | 114 | 2108 | 1292
COREOPSIS | 805.7 | 61 x 4.10 | 0.0359 | 36.9 | 120 | 2216 | 1331
JASSAMINE | 886.7 | 61 x 4.30 | 0.0327 | 38.7 | 132 | 2442 | 1410
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAAC Gremany
All Aluminum Alloy Conductors (AAAC)
(a) Description:-
* All Aluminum Alloy wires , stranded in successive layers , in opposite direction to form the Aluminum stranded AAAC conductor,
(b) Application:-
* All Aluminum-Alloy Conductors (AAAC) can be used in Medium, High and Extra-High voltage transmission lines.
AAAC offers better sag performance due to the high strength-to-weight ratio provided by the aluminum-alloy.
In addition, AAAC provides a higher corrosion resistance than ACSR conductors.
They are also used a messenger to support overhead electrical cables.
(c) Technical Data:-
| Relevent Standard |  | BS EN 50182, DIN 48201-6, IEC 61089, ASTM B 399
| Conductor |  | Plain bare All Aluminum Alloy
| Minimum bending Radius |  | 10 x outer diameter
| Packing Condition |  | Our standard length on Wooden Drum / or according to customer request
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Minimum | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
A- BS EN 50182 (GREMANY) & DIN 48201-6
PO-LT11-00-01-U0 | 16 | 7 x 1.70 | 2.071 | 5.1 | 4.69 | 43.4 | 105
PO-LT12-00-01-U0 | 25 | 7 x 2.10 | 1.3566 | 6.3 | 7.15 | 66.2 | 135
PO-LT13-00-01-U0 | 35 | 7 x 2.50 | 0.9572 | 7.5 | 10.14 | 93.8 | 170
PO-LT14-00-01-U0 | 50 | 7 x 3.00 | 0.6647 | 9 | 14.6 | 135.1 | 210
PO-LT14-00-01-U0 | 50 | 19 x 1.80 | 0.6841 | 9 | 14.26 | 132.7 | 210
PO-LT15-00-01-U0 | 70 | 19 x 2.10 | 0.5026 | 10.5 | 19.41 | 180.7 | 255
PO-LT16-00-01-U0 | 95 | 19 x 2.50 | 0.3546 | 12.5 | 27.51 | 256 | 320
PO-LT17-00-01-U0 | 120 | 19 x 2.80 | 0.2827 | 14 | 34.51 | 321.2 | 365
PO-LT18-00-01-U0 | 150 | 37 x 2.25 | 0.2256 | 15.8 | 43.4 | 405.3 | 425
PO-LT19-00-01-U0 | 185 | 37 x 2.50 | 0.1827 | 17.5 | 53.58 | 500.3 | 490
PO-LT20-00-01-U0 | 240 | 61 x 2.25 | 0.1373 | 20.3 | 71.55 | 670.3 | 585
PO-LT21-00-01-U0 | 300 | 61 x 2.50 | 0.1112 | 22.5 | 88.33 | 827.5 | 670
PO-LT22-00-01-U0 | 400 | 61 x 2.89 | 0.0832 | 26 | 118.04 | 1105.9 | 810
PO-LT23-00-01-U0 | 500 | 61 x 3.23 | 0.0666 | 29.1 | 147.45 | 1381.4 | 930
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAAC U.K
All Aluminum Alloy Conductors (AAAC)
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Minimum | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
B - BS EN 50182 (United Kingdom)
BOX | 18.8 | 7 x 1.85 | 1.748 | 5.55 | 5.55 | 51.4 | 112
ACACIA | 23.8 | 7 x 2.08 | 1.3828 | 6.24 | 7.02 | 64.9 | 130
ALMOND | 30.1 | 7 x 2.34 | 1.0926 | 7.02 | 8.88 | 82.2 | 151
CEDAR | 35.5 | 7 x 2.54 | 0.9273 | 7.62 | 10.46 | 96.8 | 168
DEODAR | 42.2 | 7 x 2.77 | 0.7797 | 8.31 | 12.44 | 115.2 | 187
FIR | 47.8 | 7 x 2.95 | 0.6875 | 8.85 | 14.11 | 130.6 | 202
HAZEL | 59.9 | 7 x 3.30 | 0.5494 | 9.9 | 17.66 | 163.4 | 233
PINE | 71.6 | 7 x 3.61 | 0.4591 | 10.8 | 21.14 | 195.6 | 261
HOLLY | 84.1 | 7 x 3.91 | 0.3913 | 11.7 | 24.79 | 229.5 | 289
WILLOW | 89.7 | 7 x 4.04 | 0.3665 | 12.1 | 26.47 | 245 | 301
OAK | 118.9 | 7 x 4.65 | 0.2767 | 14 | 35.07 | 324.5 | 360
MULBERRY | 150.9 | 19 x 3.18 | 0.2192 | 15.9 | 44.52 | 414.3 | 420
ASH | 180.7 | 19 x 3.48 | 0.183 | 17.4 | 53.31 | 496.1 | 471
ELM | 221 | 19 x 3.76 | 0.1568 | 18.8 | 62.24 | 579.2 | 519
POPLAR | 239.4 | 37 x 2.87 | 0.1387 | 20.1 | 70.61 | 659.4 | 562
SYCAMORE | 303.2 | 37 x 3.23 | 0.1095 | 22.6 | 89.4 | 835.2 | 654
UPAS | 362.1 | 37 x 3.53 | 0.0917 | 24.7 | 106.82 | 997.5 | 732
YEW | 479 | 37 x 4.06 | 0.0693 | 28.4 | 141.31 | 1319.6 | 874
TOTARA | 498.1 | 37 x 4.14 | 0.0666 | 29 | 146.93 | 1372.1 | 895
RUBUS | 586.9 | 61 x 3.50 | 0.0567 | 31.5 | 173.13 | 1622 | 991
SORBUS | 659.4 | 61 x 3.71 | 0.0505 | 33.4 | 194.53 | 1822 | 1066
ARAUCARIA | 821.1 | 61 x 4.14 | 0.0406 | 37.3 | 242.24 | 2269.4 | 1221
REDWOOD | 996.2 | 61 x 4.56 | 0.0334 | 41 | 293.88 | 2753.2 | 1373
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAAC France
All Aluminum Alloy Conductors (AAAC)
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Minimum | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
C - BS EN 50182 (France)
ASTER - 22 | 22 | 7 x 2.00 | 1.4989 | 6 | 7.15 | 60 | 126
ASTER - 34.4 | 34.4 | 7 x 2.50 | 0.9593 | 7.5 | 11.17 | 93.8 | 168
ASTER - 54.6 | 54.6 | 7 x 3.15 | 0.6042 | 9.45 | 17.73 | 148.9 | 225
ASTER - 75.5 | 75.5 | 19 x 2.25 | 0.4388 | 11.3 | 24.55 | 207.4 | 278
ASTER - 117 | 117 | 19 x 2.80 | 0.2833 | 14 | 38.02 | 321.2 | 367
ASTER - 148.1 | 148.1 | 19 x 3.15 | 0.2239 | 15.8 | 48.12 | 406.5 | 427
ASTER - 181.6 | 181.6 | 37 x 2.50 | 0.1831 | 17.5 | 59.03 | 500.3 | 487
ASTER - 227.8 | 227.8 | 37 x 2.80 | 0.146 | 19.6 | 74.04 | 627.6 | 563
ASTER - 288.3 | 288.3 | 37 x 3.15 | 0.1154 | 22.1 | 93.71 | 794.3 | 655
ASTER - 266.2 | 266.2 | 37 x 3.55 | 0.0908 | 24.9 | 115.36 | 1008.9 | 764
ASTER - 570.2 | 570.2 | 61 x 3.45 | 0.0585 | 31.1 | 185.33 | 1576 | 1013
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, windemissivity coefficient of 0.6, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAAC-B IEC
All Aluminum Conductors (AAAC)
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
D - IEC 61089 (Aluminum Alloy A2 - Type B)
A2 - 16 | 18.4 | 7 x 1.83 | 1.7896 | 5.49 | 5.43 | 50.4 | 150
A2 - 25 | 28.8 | 7 x 2.29 | 1.1453 | 6.86 | 8.49 | 78.7 | 200
A2 - 40 | 46 | 7 x 2.89 | 0.7158 | 8.68 | 13.58 | 125.9 | 270
A2 - 63 | 72.5 | 7 x 3.63 | 0.4545 | 10.9 | 21.39 | 198.3 | 361
A2 - 100 | 115 | 19 x 2.78 | 0.2877 | 13.9 | 33.95 | 316.3 | 487
A2 - 125 | 144 | 19 x 3.10 | 0.2302 | 15.5 | 42.44 | 395.4 | 562
A2 - 160 | 184 | 19 x 3.51 | 0.1798 | 17.6 | 54.32 | 506.1 | 659
A2 - 200 | 230 | 19 x 3.93 | 0.1439 | 19.6 | 67.91 | 632.7 | 760
A2 - 250 | 288 | 19 x 4.39 | 0.1151 | 22 | 84.88 | 790.8 | 879
A2 - 315 | 363 | 37 x 3.53 | 0.0916 | 24.7 | 106.95 | 998.9 | 1019
A2 - 400 | 460 | 37 x 3.98 | 0.0721 | 27.9 | 135.81 | 1268.4 | 1188
A2 - 450 | 518 | 37 x 4.22 | 0.0641 | 29.6 | 152.79 | 1426.9 | 1282
A2 - 500 | 575 | 37 x 4.45 | 0.0577 | 31.2 | 169.76 | 1585.5 | 1370
A2 - 560 | 645 | 61 x 3.67 | 0.0516 | 33 | 190.14 | 1778.4 | 1472
A2 - 630 | 725 | 61 x 3.89 | 0.0458 | 35 | 213.9 | 2000.7 | 1585
A2 - 710 | 817 | 61 x 4.13 | 0.0407 | 37.2 | 241.07 | 2254.8 | 1706
A2 - 800 | 921 | 61 x 4.38 | 0.0361 | 39.5 | 271.62 | 2540.6 | 1840
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 20 °C , final temperature of 80 °C, wind velocity of 1.0 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAAC-A IEC
All Aluminum Conductors (AAAC)
Product-code | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
E - IEC 61089 (Aluminum Alloy A3 - Type A)
A3 - 16 | 18.6 | 7 x 1.84 | 1.7896 | 5.52 | 6.04 | 50.8 | 151
A3 - 25 | 29 | 7 x 2.30 | 1.1453 | 6.9 | 9.44 | 79.5 | 200
A3 - 40 | 46.5 | 7 x 2.91 | 0.7158 | 8.72 | 15.1 | 127.1 | 270
A3 - 63 | 73.2 | 7 x 3.65 | 0.4545 | 10.9 | 23.06 | 200.2 | 361
A3 - 100 | 116 | 19 x 2.79 | 0.2877 | 14 | 37.76 | 319.3 | 488
A3 - 125 | 145 | 19 x 3.12 | 0.2302 | 15.6 | 42.2 | 399.2 | 563
A3 - 160 | 186 | 19 x 3.53 | 0.1798 | 17.6 | 58.56 | 511 | 659
A3 - 200 | 232 | 19 x 3.95 | 0.1439 | 19.7 | 73.2 | 638.7 | 761
A3 - 250 | 290 | 19 x 4.41 | 0.1151 | 22.1 | 91.5 | 798.4 | 880
A3 - 315 | 366 | 37 x 3.55 | 0.0916 | 24.8 | 115.29 | 1008.4 | 1020
A3 - 400 | 465 | 37 x 4.00 | 0.0721 | 28 | 146.4 | 1280.5 | 1190
A3 - 450 | 523 | 37 x 4.24 | 0.0641 | 29.7 | 164.7 | 1440.5 | 1283
A3 - 500 | 581 | 37 x 4.47 | 0.0577 | 31.3 | 183 | 1600.6 | 1371
A3 - 560 | 651 | 61 x 3.69 | 0.0516 | 33.2 | 204.96 | 1795.3 | 1474
A3 - 630 | 732 | 61 x 3.91 | 0.0458 | 35.2 | 230.58 | 2019.8 | 1587
A3 - 710 | 825 | 61 x 4.15 | 0.0407 | 37.3 | 259.86 | 2276.2 | 1708
A3 - 800 | 930 | 61 x 4.40 | 0.0361 | 39.6 | 292.8 | 2564.8 | 1841
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 20 °C , final temperature of 80 °C, wind velocity of 1.0 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAAC ASTM B 399
All Aluminum Conductors (AAAC)
Product-code AWG or Kcmil | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
E - ASTM B 399
6 | 13.2 | 7 x 1.55 | 2.5361 | 4.65 | 4.18 | 36.2 | 91
4 | 21.1 | 7 x 1.96 | 1.586 | 5.88 | 6.69 | 57.9 | 122
2 | 33.5 | 7 x 2.47 | 0.9987 | 7.41 | 10.65 | 92 | 164
0 | 53.5 | 7 x 3.12 | 0.62592 | 9.36 | 17 | 146.8 | 221
2 / 0 | 67.3 | 7 x 3.50 | 0.49738 | 10.5 | 20.4 | 184.8 | 256
3 / 0 | 84.9 | 7 x 3.93 | 0.3945 | 11.79 | 25.7 | 233 | 296
4 / 0 | 107 | 7 x 4.42 | 0.31188 | 13.26 | 32.5 | 294.7 | 345
250 | 126 | 19 x 2.91 | 0.26509 | 14.55 | 38.8 | 346.7 | 384
300 | 152 | 19 x 3.19 | 0.22059 | 15.95 | 46.6 | 416.7 | 432
350 | 178 | 19 x 3.45 | 0.1886 | 17.25 | 52 | 487.3 | 1020
450 | 203 | 19 x 3.69 | 0.16486 | 18.45 | 59.5 | 557.5 | 521
500 | 228 | 19 x 3.91 | 0.14683 | 19.55 | 66.8 | 626 | 561
550 | 253 | 19 x 4.12 | 0.13224 | 20.6 | 74.2 | 695 | 600
600 | 279 | 37 x 3.10 | 0.11995 | 21.7 | 83.9 | 766.2 | 640
650 | 303 | 37 x 3.23 | 0.11049 | 22.61 | 91 | 831.9 | 674
700 | 330 | 37 x 3.37 | 0.1015 | 23.59 | 94.9 | 905.5 | 712
750 | 354 | 37 x 3.49 | 0.09464 | 24.43 | 101 | 971.2 | 745
800 | 381 | 37 x 3.62 | 0.08796 | 25.34 | 109 | 1045 | 781
850 | 404 | 37 x 3.73 | 0.08285 | 26.124 | 116 | 1109 | 811
900 | 456 | 37 x 3.96 | 0.07351 | 27.72 | 131 | 1250 | 876
1000 | 508 | 37 x 4.18 | 0.06597 | 29.26 | 146 | 1393 | 938
1250 | 631 | 61 x 3.63 | 0.05306 | 32.67 | 179 | 1732 | 1078
1500 | 759 | 61 x 3.98 | 0.04414 | 35.82 | 215 | 2082 | 1210
1750 | 886 | 61 x 4.30 | 0.03781 | 38.7 | 251 | 2431 | 1332
The above data is approximate and subjected to manufacturing tolerance.
Note:
the size 404 mm2 may be requested 405 mm2 as per customer request with the same above specification
the size 508 mm2 may be requested 506.7 mm2 as per customer request with the same above specification
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AAAC ASTM B 399-2
All Aluminum Conductors (AAAC)
Product-code Kcmil | Cross | Number and Nominal | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
| Sectional Area | Diameter of Wires | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | No. x mm | Ω/km | mm | KN | Kg/km | Amps
F - ASTM B 399 (ALCOA American Sizes)
Akron | 15.5 | 7 x 1.68 | 2.159 | 5.04 | 4.92 | 42.58 | 100
Alton | 24.7 | 7 x 2.12 | 1.356 | 6.36 | 7.83 | 67.8 | 135
Ames | 39.2 | 7 x 2.67 | 0.8547 | 8.01 | 12.4 | 107.5 | 181
Azusa | 62.4 | 7 x 3.37 | 0.5365 | 10.11 | 18.9 | 171.3 | 243
Anaheim | 78.6 | 7 x 3.78 | 0.4264 | 11.34 | 23.8 | 215.6 | 282
Amherst | 99.3 | 7 x 4.25 | 0.3373 | 12.75 | 30 | 272.5 | 328
Alliance | 125 | 7 x 4.77 | 0.2678 | 14.31 | 37.8 | 343.2 | 380
Butte | 159 | 19 x 3.26 | 0.2112 | 16.3 | 46.5 | 435.1 | 444
Canton | 200 | 19 x 3.66 | 0.167 | 18.3 | 58.6 | 548.5 | 516
Cairo | 236 | 19 x 3.98 | 0.1417 | 19.9 | 69.2 | 648.6 | 1020
Darien | 284 | 19 x 4.36 | 0.1181 | 21.8 | 83.1 | 778.3 | 645
Elgin | 331 | 19 x 4.71 | 0.1012 | 23.55 | 97 | 908.3 | 713
Flint | 375 | 37 x 3.59 | 0.08944 | 25.13 | 107 | 1028 | 772
Gereeley | 470 | 37 x 4.02 | 0.07133 | 28.14 | 135 | 1289 | 893
1077.4 | 547 | 37 x 3.38 | 0.0612 | 23.66 | 156 | 1502 | 914
1165.1 | 590 | 61 x 3.51 | 0.05675 | 31.59 | 167 | 1620 | 1033
1259.6 | 638 | 61 x 3.65 | 0.05248 | 32.85 | 181 | 1751 | 1085
1348.8 | 685 | 61 x 3.78 | 0.04893 | 34.02 | 194 | 1878 | 1134
1439.2 | 729 | 61 x 3.90 | 0.04597 | 35.1 | 207 | 1999 | 1179
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## ACSR Gremany
Aluminum Conductor Steel Reinforced (ACSR)
(a) Description:-
* An outer layer of Aluminum conductor concentrically stranded over the central core of galvanized solid or stranded steel wires to form Aluminum steel reinforced conductor.
(b) Application:-
* Aluminum Conductors, Steel-Reinforced (ACSR) can be used in Medium, High and Extra-High voltage transmission lines; also used for primary and secondary distribution lines.
The combination of aluminum and steel in the conductor design offers both efficient conductivity and high tensile strength making ACSR the most economical solution
for overhead power transmission and distribution projects.
(c) Technical Data:-
| Relevent Standard |  | BS EN 50182, BS 215-2, DIN 48204, IEC 61089, ASTM B 232
| Conductor |  | Plain bare hard drawn Aluminum - H14 over the central core of galvanized solid or stranded steel wires
| Minimum bending Radius |  | 10 x outer diameter
| Packing Condition |  | Our standard length on Wooden Drum / or according to customer request
Product-code | Total Cross | Number and Nominal |  | Max. D.C. Conductor | Approx. Overall | Minimum | Approx. | Rated
| Sectional Area | Diameter of Wires |  | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | Aluminum No. x mm | Steel No. x mm | Ω/km | mm | KN | Kg/km | Amps
A - BS EN 50182 (GREMANY) & DIN 48204
PO-RTAA-00-01-U0 | 16 / 2.5 | 6 x 1.80 | 1 x 1.80 | 1.8769 | 5.4 | 5.8 | 61.6 | 105
PO-RTAB-00-01-U0 | 25 / 4 | 6 x 2.25 | 1 x 2.25 | 1.2012 | 6.75 | 8.95 | 96.3 | 140
PO-RTAC-00-01-U0 | 35 / 6 | 6 x 2.70 | 1 x 2.70 | 0.8342 | 8.1 | 12.37 | 138.7 | 170
PO-RTAD-00-01-U0 | 44 / 32 | 14 x 20 | 7 x 2.40 | 0.6574 | 11.2 | 44.24 | 369.3 | 209
PO-RTAE-00-01-U0 | 50 / 8 | 6 x 3.20 | 1 x 3.20 | 0.5939 | 9.6 | 16.81 | 194.8 | 210
PO-RTAF-00-01-U0 | 50 / 30 | 12 x 2.33 | 7 x 2.33 | 0.5644 | 11.7 | 42.98 | 374.7 | 227
PO-RTAG-00-01-U0 | 70 / 12 | 26 x 1.85 | 7 x 1.44 | 0.4132 | 11.7 | 26.27 | 282.2 | 290
PO-RTAH-00-01-U0 | 95 / 15 | 26 x 2.15 | 7 x 1.67 | 0.306 | 13.6 | 34.93 | 380.6 | 350
PO-RTAI-00-01-U0 | 95 / 55 | 12 x 3.20 | 7 x 3.20 | 0.2992 | 16 | 77.85 | 706.8 | 367
PO-RTAJ-00-01-U0 | 105 / 75 | 14 x 3.10 | 19 x 2.25 | 0.2742 | 17.5 | 105.82 | 885.3 | 394
PO-RTAK-00-01-U0 | 120 / 20 | 26 x 2.44 | 7 x 1.90 | 0.2376 | 15.5 | 44.5 | 491 | 410
PO-RTAL-00-01-U0 | 120 / 70 | 12 x 3.60 | 7 x 3.60 | 0.2364 | 18 | 97.92 | 894.5 | 427
PO-RTAM-00-01-U0 | 125 / 30 | 30 x 2.33 | 7 x 2.33 | 0.226 | 16.3 | 56.41 | 587 | 425
PO-RTAN-00-01-U0 | 150 / 25 | 26 x 2.70 | 7 x 2.10 | 0.194 | 17.1 | 53.67 | 600.8 | 470
PO-RTAO-00-01-U0 | 170 / 40 | 30 x 2.70 | 7 x 2.70 | 0.1683 | 18.9 | 74.89 | 788.2 | 520
PO-RTAP-00-01-U0 | 185 / 30 | 26 x 3.00 | 7 x 2.33 | 0.1571 | 19 | 65.27 | 741 | 535
PO-RTAQ-00-01-U0 | 210 / 35 | 26 x 3.20 | 7 x 2.49 | 0.1381 | 20.3 | 73.36 | 844.1 | 590
PO-RTAR-00-01-U0 | 210 / 50 | 30 x 3.00 | 7 x 3.00 | 0.1363 | 21 | 92.46 | 973.1 | 610
PO-RTAS-00-01-U0 | 230 / 30 | 24 x 3.50 | 7 x 2.33 | 0.125 | 21 | 72.13 | 870.9 | 630
PO-RTAT-00-01-U0 | 240 / 40 | 26 x 3.45 | 7 x 2.68 | 0.1188 | 21.8 | 85.12 | 980.1 | 645
PO-RTAU-00-01-U0 | 265 / 35 | 24 x 3.74 | 7 x 2.49 | 0.1095 | 22.4 | 81.04 | 994.4 | 680
PO-RTAV-00-01-U0 | 300 / 50 | 26 x 3.86 | 7 x 3.00 | 0.0949 | 24.4 | 105.09 | 1227.3 | 740
PO-RTAW-00-01-U0 | 305 / 40 | 54 x 2.68 | 7 x 2.68 | 0.0949 | 24.1 | 96.8 | 1151.2 | 740
PO-RTAX-00-01-U0 | 340 / 30 | 48 x 3.00 | 7 x 2.33 | 0.0852 | 25 | 91.71 | 1171.2 | 790
PO-RTAY-00-01-U0 | 380 / 50 | 54 x 3.00 | 7 x 3.00 | 0.0758 | 27 | 121.3 | 1442.5 | 840
PO-RTAZ-00-01-U0 | 385 / 35 | 48 x 3.20 | 7 x 2.49 | 0.0749 | 26.7 | 102.56 | 1333.6 | 850
PO-RTBA-00-01-U0 | 435 / 55 | 54 x 3.20 | 7 x 3.20 | 0.0666 | 28.8 | 133.59 | 1641.3 | 900
PO-RTBB-00-01-U0 | 450 / 40 | 48 x 3.45 | 7 x 2.68 | 0.0644 | 28.7 | 119.05 | 1549.1 | 920
PO-RTBC-00-01-U0 | 490 / 65 | 54 x 3.40 | 7 x 3.40 | 0.059 | 30.6 | 150.81 | 1852.9 | 960
PO-RTBD-00-01-U0 | 495 / 35 | 45 x 3.74 | 7 x 2.49 | 0.0584 | 29.9 | 117.96 | 1632.6 | 985
PO-RTBE-00-01-U0 | 510 / 45 | 48 x 3.68 | 7 x 2.87 | 0.0566 | 30.7 | 133.31 | 1765.3 | 995
PO-RTBF-00-01-U0 | 550 / 70 | 54 x 3.60 | 7 x 3.60 | 0.0526 | 32.4 | 166.32 | 2077.2 | 1020
PO-RTBG-00-01-U0 | 560 / 50 | 48 x 3.86 | 7 x 3.00 | 0.0515 | 32.2 | 146.28 | 1939.5 | 1040
PO-RTBH-00-01-U0 | 570 / 40 | 45 x 4.02 | 7 x 2.60 | 0.0506 | 32.2 | 136.4 | 1887.1 | 1050
PO-RTBI-00-01-U0 | 650 / 45 | 45 x 4.30 | 7 x 2.87 | 0.0442 | 34.4 | 156.18 | 2159.9 | 1120
PO-RTBJ-00-01-U0 | 680 / 85 | 54 x 4.00 | 19 x 2.40 | 0.0426 | 36 | 206.56 | 2549.7 | 1150
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## ACSR U.K
Aluminum Conductor Steel Reinforced (ACSR)
Product-code | Total Cross | Number and Nominal |  | Max. D.C. Conductor | Approx. Overall | Minimum | Approx. | Rated
| Sectional Area | Diameter of Wires |  | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | Aluminum No. x mm | Steel No. x mm | Ω/km | mm | KN | Kg/km | Amps
B - BS EN 50182 (United Kingdom)
MOLE | 12.4 | 6 x 1.50 | 1 x 1.50 | 2.7027 | 4.5 | 4.14 | 42.8 | 86
SQUIRREL | 24.5 | 6 x 2.11 | 1 x 2.11 | 1.3659 | 6.33 | 7.87 | 84.7 | 133
GOPHER | 30.6 | 6 x 2.36 | 1 x 2.36 | 1.0919 | 7.08 | 9.58 | 106 | 153
WEASEL | 36.9 | 6 x 2.59 | 1 x 2.59 | 0.9065 | 7.77 | 11.38 | 127.6 | 172
FOX | 42.8 | 6 x 2.79 | 1 x 2.79 | 0.7812 | 8.37 | 13.21 | 148.1 | 189
FERRET | 49.5 | 6 x 3.00 | 1 x 3.00 | 0.6757 | 9 | 15.27 | 171.2 | 208
RABBIT | 61.7 | 6 x 3.35 | 1 x 3.35 | 0.5419 | 10.1 | 18.42 | 213.5 | 240
MINK | 73.6 | 6 x 3.66 | 1 x 3.66 | 0.454 | 11 | 21.67 | 254.9 | 268
SKUNK | 100.1 | 12 x 2.59 | 7 x 2.59 | 0.4568 | 13 | 52.79 | 463 | 280
BEAVER | 87.5 | 6 x 3.99 | 1 x 3.99 | 0.382 | 12 | 25.76 | 302.9 | 300
HORSE | 116.2 | 12 x 2.79 | 7 x 2.79 | 0.3936 | 14 | 61.26 | 537.3 | 308
RACOON | 92 | 6 x 4.09 | 1 x 4.09 | 0.3635 | 12.3 | 27.06 | 318.3 | 309
OTIER | 97.9 | 6 x 4.22 | 1 x 4.22 | 0.3415 | 12.7 | 28.81 | 338.8 | 322
CAT | 111.3 | 6 x 4.50 | 1 x 4.50 | 0.3003 | 13.5 | 32.76 | 385.3 | 349
HARE | 122.5 | 6 x 4.72 | 1 x 4.72 | 0.273 | 14.2 | 36.04 | 423.8 | 372
DOG | 118.5 | 6 x 4.72 | 7 x 1.57 | 0.2733 | 14.2 | 32.65 | 394 | 371
COYOTE | 151.8 | 26 x 2.54 | 7 x 1.91 | 0.2192 | 15.9 | 45.86 | 520.7 | 428
COUGAR | 138.8 | 18 x 3.05 | 1 x 3.05 | 0.2188 | 15.3 | 29.74 | 418.8 | 424
TIGER | 161.9 | 30 x 2.36 | 7 x 2.36 | 0.2202 | 16.5 | 57.87 | 602.2 | 432
WOLF | 194.9 | 30 x 2.59 | 7 x 2.59 | 0.1829 | 18.1 | 68.91 | 725.3 | 487
DINGO | 167.5 | 18 x 3.35 | 1 x 3.35 | 0.1814 | 16.8 | 35.87 | 505.2 | 478
LYNX | 226.2 | 30 x 2.79 | 7 x 2.79 | 0.1576 | 19.5 | 79.97 | 841.6 | 536
CARACAL | 194.5 | 18 x 3.61 | 1 x 3.61 | 0.1562 | 18.1 | 40.74 | 586.7 | 526
PANTHER | 261.5 | 30 x 3.00 | 7 x 3.00 | 0.1363 | 21 | 92.46 | 973.1 | 588
JAGUAR | 222.3 | 18 x 3.86 | 1 x 3.86 | 0.1366 | 19.3 | 46.57 | 670.8 | 573
LION | 293.9 | 30 x 3.18 | 7 x 3.18 | 0.1213 | 22.3 | 100.47 | 1093.4 | 634
BEAR | 326.1 | 30 x 3.35 | 7 x 3.35 | 0.1093 | 23.5 | 111.5 | 1213.4 | 678
GOAT | 400 | 30 x 3.71 | 7 x 3.71 | 0.0891 | 26 | 135.13 | 1488.2 | 773
SHEEP | 462.6 | 30 x 3.99 | 7 x 3.99 | 0.0771 | 27.9 | 156.3 | 1721.3 | 848
ANTELOPE | 422.6 | 54 x 2.97 | 7 x 2.97 | 0.0773 | 26.7 | 118.88 | 1413.8 | 836
BISON | 431.2 | 54 x 3.00 | 7 x 3.00 | 0.0758 | 27 | 121.3 | 1442.5 | 847
DEER | 529.8 | 30 x 4.27 | 7 x 4.27 | 0.0673 | 29.9 | 179 | 1971.4 | 925
ZEBRA | 484.5 | 54 x 3.18 | 7 x 3.18 | 0.0674 | 28.6 | 131.92 | 1620.8 | 913
ELK | 588.5 | 30 x 4.50 | 7 x 4.50 | 0.0606 | 31.5 | 198.8 | 2189.5 | 989
CAMEL | 538.7 | 54 x 3.35 | 7 x 3.35 | 0.0608 | 30.2 | 146.4 | 1798.8 | 975
MOOSE | 597 | 54 x 3.53 | 7 x 3.53 | 0.0547 | 31.8 | 159.92 | 1997.3 | 1043
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec., solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## ACSR IEC
Aluminum Conductor Steel Reinforced (ACSR)
Product-code | Total Cross | Number and Nominal |  | Max. D.C. Conductor | Approx. Overall | Minimum | Approx. | Rated
| Sectional Area | Diameter of Wires |  | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | Aluminum No. x mm | Steel No. x mm | Ω/km | mm | KN | Kg/km | Amps
C - IEC 61089 (A1/S1A)
A1/S1A - 16 | 18.7 | 6 x 1.84 | 1 x 1.84 | 1.7934 | 5.53 | 6.08 | 64.6 | 149
A1/S1A - 25 | 29.2 | 6 x 2.30 | 1 x 2.30 | 1.1478 | 6.91 | 9.13 | 100.9 | 198
A1/S1A - 40 | 46.7 | 6 x 2.91 | 1 x 2.91 | 0.7174 | 8.74 | 14.4 | 161.5 | 267
A1/S1A - 63 | 73.5 | 6 x 3.66 | 1 x 3.66 | 0.4555 | 11 | 21.63 | 254.4 | 358
A1/S1A - 100 | 117 | 6 x 4.61 | 1 x 4.61 | 0.2869 | 13.8 | 34.33 | 403.8 | 481
A1/S1A - 125 | 132 | 18 x 2.97 | 1 x 2.97 | 0.2304 | 14.9 | 29.17 | 397.9 | 549
A1/S1A - 125 | 145 | 26 x 2.47 | 7 x 1.92 | 0.231 | 15.7 | 45.69 | 503.9 | 557
A1/S1A - 160 | 169 | 18 x 3.36 | 1 x 3.36 | 0.18 | 16.8 | 36.18 | 509.3 | 643
A1/S1A - 160 | 186 | 26 x 2.80 | 7 x 2.18 | 0.1805 | 17.7 | 57.69 | 644.9 | 652
A1/S1A - 200 | 211 | 18 x 3.76 | 1 x 3.76 | 0.144 | 18.8 | 44.22 | 636.7 | 743
A1/S1A - 200 | 233 | 26 x 3.13 | 7 x 3.43 | 0.1444 | 19.8 | 70.13 | 806.2 | 754
A1/S1A - 250 | 275 | 22 x 3.80 | 7 x 2.11 | 0.1154 | 21.6 | 68.72 | 880.6 | 865
A1/S1A - 250 | 291 | 26 x 3.50 | 7 x 2.72 | 0.1155 | 22.2 | 87.67 | 1007.7 | 872
A1/S1A - 315 | 337 | 45 x 2.99 | 7 x 1.99 | 0.0917 | 23.9 | 79.03 | 1039.6 | 998
A1/S1A - 315 | 366 | 26 x 3.93 | 7 x 3.05 | 0.0917 | 24.9 | 106.83 | 1269.7 | 1012
A1/S1A - 400 | 428 | 45 x 3.36 | 7 x 2.24 | 0.0722 | 26.9 | 98.36 | 1320.1 | 1164
A1/S1A - 400 | 452 | 54 x 3.07 | 7 x 3.07 | 0.0723 | 27.9 | 123.04 | 1510.3 | 1173
A1/S1A - 450 | 481 | 45 x 3.57 | 7 x 2.38 | 0.0642 | 28.5 | 107.47 | 1485.2 | 1255
A1/S1A - 450 | 508 | 54 x 3.26 | 7 x 3.26 | 0.0643 | 29.3 | 138.42 | 1699.1 | 1266
A1/S1A - 500 | 535 | 45 x 3.76 | 7 x 2.51 | 0.0578 | 30.1 | 119.41 | 1650.2 | 1343
A1/S1A - 500 | 565 | 54 x 3.43 | 7 x 3.43 | 0.0578 | 30.9 | 153.8 | 1887.9 | 1355
A1/S1A - 560 | 599 | 45 x 3.98 | 7 x 2.65 | 0.0516 | 31.8 | 133.74 | 1848.2 | 1444
A1/S1A - 560 | 631 | 54 x 3.63 | 19 x 2.18 | 0.0516 | 32.7 | 172.59 | 2103.4 | 1458
A1/S1A - 630 | 674 | 45 x 4.22 | 7 x 2.81 | 0.0459 | 33.8 | 150.45 | 2079.2 | 1557
A1/S1A - 630 | 710 | 54 x 3.85 | 19 x 2.31 | 0.0459 | 34.7 | 191.77 | 2366.3 | 1572
A1/S1A - 710 | 759 | 45 x 4.48 | 7 x 2.99 | 0.0407 | 35.9 | 169.56 | 2343.2 | 1680
A1/S1A - 710 | 800 | 54 x 4.09 | 19 x 2.45 | 0.0407 | 36.8 | 216.12 | 2666.8 | 1696
A1/S1A - 800 | 901 | 54 x 4.34 | 19 x 2.61 | 0.0362 | 39.1 | 243.52 | 3004.9 | 1828
The above data is approximate and subjected to manufacturing tolerance.
Note:
1) Other types of ACSR as per IEC 61089 (A1/S1B, A1/S2A, A1/S2B & A1/S3A) are available as per customer request
2) The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 20 °C , final temperature of 80 °C, wind velocity of 1.0 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## ACSR BS 215-2
Aluminum Conductor Steel Reinforced (ACSR)
Product-code | Total Cross | Number and Nominal |  | Max. D.C. Conductor | Approx. Overall | Minimum | Approx. | Rated
| Sectional Area | Diameter of Wires |  | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | Aluminum No. x mm | Steel No. x mm | Ω/km | mm | KN | Kg/km | Amps
D - BS 215-2
GOPHER | 25 | 6 x 2.36 | 1 x 2.36 | 1.093 | 7.08 | 9.61 | 106 | 153
WEASEL | 30 | 6 x 2.59 | 1 x 2.59 | 0.9077 | 7.77 | 11.45 | 128 | 172
FERRET | 40 | 6 x 3.00 | 1 x 3.00 | 0.6766 | 9 | 15.2 | 172 | 208
RABBIT | 50 | 6 x 3.35 | 1 x 3.35 | 0.5426 | 10.05 | 18.35 | 214 | 240
HORSE | 70 | 12 x 2.79 | 7 x 2.79 | 0.3936 | 13.95 | 61.2 | 538 | 308
DOG | 100 | 6 x 4.72 | 7 x 1.57 | 0.2733 | 14.15 | 32.7 | 394 | 371
WOLF | 150 | 30 x 2.59 | 7 x 2.59 | 0.1828 | 18.13 | 69.2 | 726 | 487
DINGO | 150 | 18 x 3.35 | 1 x 3.35 | 0.1815 | 16.75 | 35.7 | 506 | 478
LYNX | 175 | 30 x 2.79 | 7 x 2.79 | 0.1576 | 19.53 | 79.8 | 842 | 536
CARACAL | 175 | 18 x 3.61 | 1 x 3.61 | 0.1563 | 18.05 | 41.1 | 587 | 526
PANTHER | 200 | 30 x 3.00 | 7 x 3.00 | 0.1363 | 21 | 92.25 | 974 | 588
JAGUAR | 200 | 18 x 3.86 | 1 x 3.86 | 0.1367 | 19.3 | 46.55 | 671 | 573
ZEBRA | 400 | 54 x 3.18 | 7 x 3.18 | 0.0674 | 28.62 | 131.9 | 1621 | 913
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## ACSR ASTM B 232
Aluminum Conductor Steel Reinforced (ACSR)
Product-code | Aluminum Cross |  | Number and Nominal |  | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
| Sectional Area |  | Diameter of Wires |  | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| kcmil | mm2 | Aluminum No. x mm | Steel No. x mm | Ω/km | mm | KN | Kg/km | Amps
E - ASTM B 232
TURKEY | 26.24 | 13.3 | 6 x 1.68 | 1 x 1.68 | 2.1569 | 5.03 | 5.2931 | 53.6 | 99
THRUSH | 330.9 | 167.7 | 6 x 1.89 | 1 x 1.89 | 1.7043 | 5.66 | 0 | 67.7189
SWAN | 41.74 | 21.2 | 6 x 2.12 | 1 x 2.12 | 1.3545 | 6.35 | 8.2733 | 85.3368 | 133
SWANATE | 41.74 | 21.2 | 7 x 1.96 | 1 x 2.61 | 1.3583 | 6.53 | 10.4973 | 99.6216 | 134
SPARROW | 66.36 | 33.6 | 6 x 2.67 | 1 x 2.67 | 0.854 | 8.03 | 12.6768 | 135.7056 | 179
SPARATE | 66.36 | 33.6 | 7 x 2.47 | 1 x 3.3 | 0.8553 | 8.26 | 16.1907 | 158.6654 | 180
GROUSE ** | 80 | 40.5 | 8 x 2.54 | 1 x 4.24 | 0.7112 | 9.32 | 25.487 | 221.4144 | 204
ROBIN | 83.69 | 42.4 | 6 x 3 | 1 x 3 | 0.6764 | 8.99 | 15.7904 | 171.12 | 208
PETREL** | 101.8 | 51.6 | 12 x 2.34 | 7 x 2.34 | 0.5614 | 11.71 | 49.8176 | 377.6544 | 245
RAVEN | 105.6 | 53.5 | 6 x 3.37 | 1 x 3.37 | 0.536 | 10.11 | 19.4822 | 216.0576 | 241
MINORCA ** | 110.8 | 56.1 | 12 x 2.44 | 7 x 2.44 | 0.5163 | 12.22 | 54.2656 | 411.1344 | 259
QUAIL | 133.1 | 67.4 | 6 x 3.78 | 1 x 3.78 | 0.4261 | 11.35 | 23.5744 | 272.0064 | 279
LEGHORN ** | 134.6 | 68.2 | 12 x 2.69 | 7 x 2.69 | 0.4248 | 13.46 | 65.8304 | 499.224 | 293
GUINEA ** | 159 | 80.6 | 12 x 2.92 | 7 x 2.92 | 0.3605 | 14.63 | 77.3952 | 589.6944 | 326
PIGEON | 167.8 | 85 | 6 x 4.25 | 1 x 4.25 | 0.337 | 12.75 | 29.4458 | 342.984 | 324
DOTTEREL** | 176.9 | 89.6 | 12 x 3.08 | 7 x 3.08 | 0.324 | 15.42 | 84.0672 | 656.0592 | 349
DORKING ** | 190.8 | 96.7 | 12 x 3.2 | 7 x 3.2 | 0.3002 | 16.03 | 90.7392 | 707.8416 | 367
BRAHMA ** | 203.2 | 103 | 16 x 2.86 | 19 x 2.48 | 0.2818 | 18.14 | 138.3328 | 1003.8048 | 392
COCHIN ** | 211.3 | 107 | 12 x 3.37 | 7 x 3.37 | 0.2707 | 16.87 | 100.5248 | 783.8784 | 392
PENGUIN | 211.6 | 107 | 6 x 4.77 | 1 x 4.77 | 0.2676 | 14.3 | 37.1408 | 432.7104 | 376
WAXWING | 266.8 | 135 | 18 x 3.09 | 1 x 3.09 | 0.2136 | 15.47 | 30.6912 | 430.1808 | 430
PARTRIDGE | 266.8 | 135 | 26 x 2.57 | 7 x 2 | 0.2148 | 16.31 | 50.2624 | 545.9472 | 436
OSTRISH | 300 | 152 | 26 x 2.73 | 7 x 2.12 | 0.1904 | 17.27 | 56.4896 | 613.3536 | 471
MERLIN | 336.4 | 170 | 18 x 3.47 | 1 x 3.47 | 0.1694 | 17.37 | 38.6976 | 542.8224 | 500
LINNET | 336.4 | 170 | 26 x 2.89 | 7 x 2.25 | 0.1699 | 18.29 | 62.7168 | 687.456 | 506
ORIOLE | 336.4 | 170 | 30 x 2.69 | 7 x 2.69 | 0.1703 | 18.82 | 76.9504 | 783.2832 | 510
CHICKADEE | 397.5 | 201 | 18 x 3.77 | 1 x 3.77 | 0.1435 | 18.87 | 44.0352 | 641.328 | 556
BRANT | 397.5 | 201 | 24 x 3.27 | 7 x 2.18 | 0.1437 | 19.61 | 64.9408 | 760.9632 | 562
IBIS | 397.5 | 201 | 26 x 3.14 | 7 x 2.44 | 0.1439 | 19.89 | 72.5024 | 812.448 | 564
LARK | 397.5 | 201 | 30 x 2.92 | 7 x 2.92 | 0.1446 | 20.47 | 90.2944 | 925.2384 | 567
PELICAN | 477 | 242 | 18 x 4.14 | 1 x 4.14 | 0.119 | 20.68 | 52.4864 | 769.7424 | 627
FLICKER | 477 | 242 | 24 x 3.58 | 7 x 2.39 | 0.1199 | 21.49 | 76.5056 | 913.4832 | 631
HAWK | 477 | 242 | 26 x 3.44 | 7 x 2.68 | 0.1199 | 21.79 | 86.736 | 975.0864 | 631
HEN | 477 | 242 | 30 x 3.2 | 7 x 3.2 | 0.1204 | 22.43 | 105.8624 | 1110.6432 | 638
OSPREY | 556.5 | 282 | 18 x 4.47 | 1 x 4.47 | 0.1021 | 22.33 | 60.9376 | 897.7104 | 691
PARAKEET | 556.5 | 282 | 24 x 3.87 | 7 x 2.58 | 0.1026 | 23.22 | 88.0704 | 1065.5568 | 695
DOVE | 556.5 | 282 | 26 x 3.72 | 7 x 2.89 | 0.1025 | 23.55 | 100.5248 | 1138.6176 | 701
EAGLE | 556.5 | 282 | 30 x 3.46 | 7 x 3.46 | 0.103 | 24.21 | 123.6544 | 1295.6016 | 705
PEACOCK | 605 | 307 | 24 x 4.03 | 7 x 2.69 | 0.0946 | 24.21 | 96.0768 | 1158.8544 | 735
SQUAB | 605 | 307 | 26 x 3.87 | 7 x 3.01 | 0.0947 | 24.54 | 108.0864 | 1236.9744 | 738
WOOD DUCK | 605 | 307 | 30 x 3.61 | 7 x 3.61 | 0.0946 | 25.25 | 128.5472 | 1408.392 | 735
TEAL | 605 | 307 | 30 x 3.61 | 19 x 2.16 | 0.0946 | 23.98 | 133.44 | 1396.6368 | 735
KINGBIRD | 636 | 322 | 18 x 4.78 | 1 x 4.78 | 0.0893 | 23.88 | 69.8336 | 1026.5712 | 753
SWIFT | 636 | 322 | 36 x 3.38 | 1 x 3.38 | 0.0892 | 23.62 | 61.3824 | 956.4864 | 751
ROOK | 636 | 322 | 24 x 4.14 | 7 x 2.76 | 0.0897 | 24.82 | 100.5248 | 1217.4816 | 760
GROSBEAK | 636 | 322 | 26 x 3.97 | 7 x 3.09 | 0.09 | 25.15 | 112.0896 | 1300.8096 | 762
SCOTER | 636 | 322 | 30 x 3.7 | 7 x 3.7 | 0.09 | 25.88 | 135.2192 | 1480.7088 | 762
EGRET | 636 | 322 | 30 x 3.7 | 19 x 2.22 | 0.09 | 25.88 | 140.112 | 1468.9536 | 762
FLAMINGO | 666.6 | 338 | 24 x 4.23 | 7 x 2.82 | 0.0859 | 25.4 | 105.4176 | 1276.5552 | 782
GANNET | 666.6 | 338 | 26 x 4.07 | 7 x 3.16 | 0.0856 | 25.76 | 117.4272 | 1363.3056 | 787
STILT | 715.5 | 363 | 24 x 4.39 | 7 x 2.92 | 0.0797 | 26.31 | 113.424 | 1370.448 | 820
STARLING | 715.5 | 363 | 26 x 4.21 | 7 x 3.28 | 0.08 | 26.7 | 126.3232 | 1463.7456 | 822
REDWING | 715.5 | 363 | 30 x 3.92 | 19 x 2.35 | 0.0802 | 27.46 | 153.9008 | 1650.6384 | 828
COOT | 795 | 403 | 36 x 3.77 | 1 x 3.77 | 0.0717 | 26.42 | 74.7264 | 1195.7568 | 865
CUCKOO | 795 | 403 | 24 x 4.62 | 7 x 3.08 | 0.072 | 27.74 | 124.0992 | 1522.224 | 876
DRAKE | 795 | 403 | 26 x 4.44 | 7 x 3.45 | 0.072 | 28.14 | 140.112 | 1626.384 | 876
TERN | 795 | 403 | 45 x 3.38 | 7 x 2.25 | 0.0717 | 27 | 98.3008 | 1331.76 | 865
CONDOR | 795 | 403 | 54 x 3.08 | 7 x 3.08 | 0.072 | 27.74 | 125.4336 | 1520.736 | 876
MALLARD | 795 | 403 | 30 x 4.14 | 19 x 2.48 | 0.0719 | 28.96 | 170.8032 | 1836.0432 | 887
RUDDY | 900 | 456 | 45 x 3.59 | 7 x 2.4 | 0.0636 | 28.73 | 108.5312 | 1507.344 | 940
CANARY | 900 | 456 | 54 x 3.28 | 7 x 3.28 | 0.0635 | 29.51 | 141.8912 | 1723.104 | 948
CATBIRD | 954 | 483 | 36 x 4.14 | 1 x 4.14 | 0.0595 | 28.96 | 88.0704 | 1434.432 | 973
RAIL | 954 | 483 | 45 x 3.7 | 7 x 2.47 | 0.0599 | 29.59 | 115.2032 | 1598.112 | 976
CARDINAL | 954 | 483 | 54 x 3.38 | 7 x 3.38 | 0.0598 | 30.38 | 150.3424 | 1825.9248 | 985
TANAGER | 1033.5 | 524 | 36 x 4.3 | 1 x 4.3 | 0.0551 | 30.12 | 95.1872 | 1553.472 | 1022
ORTOLAN | 1033.5 | 524 | 45 x 3.85 | 7 x 2.57 | 0.0553 | 30.78 | 123.2096 | 1730.544 | 1027
CURLEW | 1033.5 | 524 | 54 x 3.51 | 7 x 3.51 | 0.0554 | 31.62 | 162.7968 | 1977.552 | 1034
BLUEJAY | 1113 | 564 | 45 x 4 | 7 x 2.66 | 0.0512 | 31.98 | 132.5504 | 1865.952 | 1078
FINCH | 1113 | 564 | 54 x 3.65 | 19 x 2.19 | 0.0515 | 32.84 | 173.9168 | 2127.84 | 1084
BUNTING | 1192.5 | 604 | 45 x 4.14 | 7 x 2.76 | 0.0478 | 33.07 | 142.336 | 1996.896 | 1126
GRACKLE | 1192.5 | 604 | 54 x 3.77 | 19 x 2.27 | 0.0483 | 33.99 | 186.3712 | 2278.128 | 1129
SKYLARK | 1272 | 645 | 36 x 4.78 | 1 x 4.78 | 0.0446 | 33.43 | 117.4272 | 1913.568 | 1167
BITTERN | 1272 | 645 | 45 x 4.27 | 7 x 2.85 | 0.045 | 34.16 | 151.6768 | 2130.816 | 1170
PHEASANT | 1272 | 645 | 54 x 3.9 | 19 x 2.34 | 0.0451 | 35.1 | 193.9328 | 2431.392 | 1178
DIPPER | 1351.5 | 685 | 45 x 4.4 | 7 x 2.93 | 0.0423 | 35.2 | 161.0176 | 2263.248 | 1216
MARTIN | 1351.5 | 685 | 54 x 4.02 | 19 x 2.41 | 0.0425 | 36.17 | 205.9424 | 2581.68 | 1223
BOBOLINK | 1431 | 725 | 45 x 4.53 | 7 x 3.02 | 0.0399 | 36.25 | 170.3584 | 2397.168 | 1261
PLOVER | 1431 | 725 | 54 x 4.14 | 19 x 2.48 | 0.04 | 37.21 | 218.3968 | 2734.944 | 1269
NUTHATCH | 1510.5 | 765 | 45 x 4.65 | 7 x 3.1 | 0.0379 | 37.24 | 178.3648 | 2529.6 | 1302
PARROT | 1510.5 | 765 | 54 x 4.25 | 19 x 2.55 | 0.038 | 38.23 | 229.9616 | 2883.744 | 1311
LAPWING | 1590 | 806 | 45 x 4.78 | 7 x 3.18 | 0.0359 | 38.2 | 187.7056 | 2663.52 | 1345
FALCON | 1590 | 806 | 54 x 4.36 | 19 x 2.62 | 0.0361 | 39.24 | 242.416 | 3038.496 | 1353
The above data is approximate and subjected to manufacturing tolerance.
Note:
** ACSR with High Strength Steel Wires
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## ACSR-AW ASTM B 549
Aluminum Conductor Aluminum Clad Steel Reinforced (ACSR / AW)
(a) Description:-
* An outer layer of Aluminum conductor concentrically stranded over the central core of Aluminum clad Steel solid or stranded to form Aluminum Conductor Aluminum Clad Steel Reinforced.
(b) Application:-
* Aluminum Conductors, Aluminum-Clad Steel Reinforced (ACSR/AW) can be used in Medium, High and Extra-High voltage transmission lines; also used for earth wires.
In comparison with ACSR conductors, ACSR/AW conductors have considerable technical and economical advantages in overhead lines.
Its lower weight combined with its higher current carrying capacity and corrosion protection provide a longer life cycle, reduction in energy losses and significant cost saving during the operation of the line.
(c) Technical Data:-
|  |  | Relevent Standard |  |  | IEC 61089, ASTM B 549
|  |  | Conductor |  |  | Plain bare hard drawn Aluminum - H14 over the central core of Aluminum clad steel solid or stranded wires
|  |  | Minimum bending Radius |  |  | 10 x outer diameter
|  |  | Packing Condition |  |  | Our standard length on Wooden Drum / or according to customer request
Product-code | Cross section Area Using only Aluminum strand wires |  | Approximate Cross section Area including |  | Number and Nominal |  | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
|  |  | Nominal Aluminum Area in AW strand wires |  | Diameter of Wires |  | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| kcmil | mm2 | kcmil | mm2 | Aluminum No. x mm | Aluminum Clad Steel No. x mm | Ω/km | mm | KN | Kg/km | Amps
A - ASTM B 549
4 SWAN / AW | 41.74 | 21.2 | 42.7 | 21.6 | 6 x 2.12 | 1 x 2.12 | 1.2822 | 6.35 | 8 | 81 | 137
4 SWANATE / AW | 41.74 | 21.2 | 43 | 21.8 | 7 x 1.96 | 1 x 2.61 | 1.2511 | 6.53 | 10 | 93 | 140
3 SWALLOW / AW | 52.62 | 26.7 | 53.9 | 27.3 | 6 x 2.38 | 1 x 2.38 | 1.0174 | 7.14 | 10 | 103 | 159
2 SPARROW / AW | 66.36 | 33.6 | 67.1 | 34 | 6 x 2.67 | 1 x 2.67 | 0.8084 | 8.03 | 12 | 129 | 184
2 SPARATE / AW | 66.36 | 33.6 | 67.6 | 34.3 | 7 x 2.47 | 1 x 3.3 | 0.7874 | 8.26 | 16 | 149 | 188
GROUSE / AW ** | 80 | 40.5 | 82.7 | 41.9 | 8 x 2.54 | 1 x 4.24 | 0.6359 | 9.32 | 22 | 205 | 216
1 ROBIN / AW | 83.69 | 42.4 | 85.4 | 43.3 | 6 x 3 | 1 x 3 | 0.6403 | 8.99 | 15 | 162 | 213
PETREL / AW ** | 101.8 | 51.6 | 107.8 | 54.6 | 12 x 2.34 | 7 x 2.34 | 0.4684 | 11.71 | 44 | 342 | 269
RAVEN / AW | 105.6 | 63.5 | 107.7 | 54.6 | 6 x 3.37 | 1 x 3.37 | 0.5074 | 10.11 | 19 | 205 | 248
MINORCA / AW ** | 110.8 | 56.1 | 117.3 | 59.4 | 12 x 2.44 | 7 x 2.44 | 0.4308 | 12.22 | 48 | 372 | 283
2/0 QUAIL / AW | 133.1 | 67.4 | 135.2 | 68.5 | 6 x 3.78 | 1 x 3.78 | 0.4033 | 11.35 | 23 | 259 | 287
LEGHORN / AW ** | 134.6 | 68.2 | 142.7 | 72.3 | 12 x 2.69 | 7 x 2.69 | 0.3544 | 13.46 | 58 | 452 | 321
GUINEA / AW ** | 159 | 80.6 | 168 | 85.1 | 12 x 2.92 | 7 x 2.92 | 0.3008 | 14.63 | 68 | 534 | 357
3/0 PIGEON / AW | 167.8 | 85 | 170.7 | 86.5 | 6 x 4.25 | 1 x 4.25 | 0.3191 | 12.75 | 28 | 326 | 333
DOTTEREL / AW ** | 179.6 | 89.6 | 187.1 | 95 | 12 x 3.08 | 7 x 3.08 | 0.2704 | 15.42 | 75 | 594 | 382
DORKING / AW ** | 190.8 | 96.7 | 201.9 | 102 | 12 x 3.2 | 7 x 3.2 | 0.2505 | 16.03 | 81 | 641 | 402
BRAHMA / AW ** | 203.2 | 103 | 220.7 | 112 | 16 x 2.86 | 19 x 2.48 | 0.2163 | 18.14 | 121 | 894 | 448
COCHIN / AW ** | 211.3 | 107 | 223 | 113 | 12 x 3.37 | 7 x 3.37 | 0.2258 | 16.87 | 88 | 710 | 429
4/0 PENGUIN / AW | 211.6 | 107 | 215.4 | 109 | 6 x 4.77 | 1 x 4.77 | 0.2533 | 14.3 | 34 | 412 | 387
WAXWING / AW | 266.8 | 135 | 268.4 | 136 | 18 x 3.09 | 1 x 3.09 | 0.2096 | 15.47 | 30 | 421 | 435
PARTRIDGE / AW | 266.8 | 135 | 271.2 | 137 | 26 x 2.57 | 7 x 2 | 0.2035 | 16.31 | 48 | 519 | 448
OSTRISH / AW | 300 | 152 | 304.8 | 154 | 26 x 2.73 | 7 x 2.12 | 0.1804 | 17.27 | 54 | 583 | 483
MERLIN / AW | 336.4 | 170 | 337.8 | 171 | 18 x 3.47 | 1 x 3.47 | 0.1662 | 17.37 | 38 | 531 | 504
LINNET / AW | 336.4 | 170 | 341.3 | 173 | 26 x 2.89 | 7 x 2.25 | 0.1609 | 18.29 | 60 | 655 | 520
ORIOLE / AW | 336.4 | 170 | 343.7 | 174 | 30 x 2.69 | 7 x 2.69 | 0.1578 | 18.82 | 74 | 737 | 530
CHICKADEE / AW | 397.5 | 201 | 399.2 | 202 | 18 x 3.77 | 1 x 3.77 | 0.1408 | 18.87 | 44 | 628 | 561
BRANT / AW | 397.5 | 201 | 403 | 204 | 24 x 3.27 | 7 x 2.18 | 0.1377 | 19.61 | 63 | 731 | 574
IBIS / AW | 397.5 | 201 | 403.3 | 204 | 26 x 3.14 | 7 x 2.44 | 0.1363 | 19.89 | 70 | 774 | 579
LARK / AW | 397.5 | 201 | 406 | 206 | 30 x 2.92 | 7 x 2.92 | 0.1339 | 20.47 | 87 | 869 | 589
PELICAN / AW | 477.7 | 242 | 479.6 | 243 | 18 x 4.14 | 1 x 4.14 | 0.1168 | 20.68 | 51 | 755 | 632
FLICKER / AW | 477.7 | 242 | 483 | 245 | 24 x 3.58 | 7 x 2.39 | 0.1148 | 21.49 | 74 | 877 | 645
HAWK / AW | 477.7 | 242 | 484.6 | 246 | 26 x 3.44 | 7 x 2.68 | 0.1136 | 21.79 | 84 | 929 | 651
HEN / AW | 477.7 | 242 | 487.9 | 247 | 30 x 3.2 | 7 x 3.2 | 0.1115 | 22.43 | 104 | 1043 | 663
OSPREY / AW | 556.5 | 282 | 559 | 283 | 18 x 4.47 | 1 x 4.47 | 0.1002 | 22.33 | 59 | 880 | 698
PARAKEET / AW | 556.5 | 282 | 564 | 286 | 24 x 3.87 | 7 x 2.58 | 0.0983 | 23.22 | 86 | 1022 | 713
DOVE / AW | 556.5 | 282 | 564.8 | 286 | 26 x 3.72 | 7 x 2.89 | 0.0971 | 23.55 | 97 | 1083 | 720
EAGLE / AW | 556.5 | 282 | 569.7 | 289 | 30 x 3.46 | 7 x 3.46 | 0.0954 | 24.21 | 119 | 1217 | 732
PEACOCK / AW | 605 | 307 | 612.7 | 310 | 24 x 4.03 | 7 x 2.69 | 0.0906 | 24.21 | 93 | 111 | 751
SQUAB / AW | 605 | 307 | 614.6 | 311 | 26 x 3.87 | 7 x 3.01 | 0.0898 | 24.54 | 105 | 1177 | 757
WOOD DUCK / AW | 605 | 307 | 618.8 | 314 | 30 x 3.61 | 7 x 3.61 | 0.0876 | 25.25 | 126 | 1323 | 773
TEAL / AW | 605 | 307 | 618.4 | 313 | 30 x 3.61 | 19 x 2.16 | 0.0878 | 23.98 | 127 | 1314 | 761
KINGBIRD / AW | 636 | 322 | 639.4 | 324 | 18 x 4.78 | 1 x 4.78 | 0.0876 | 23.88 | 67 | 1006 | 773
SWIFT / AW | 636 | 322 | 637.7 | 323 | 36 x 3.38 | 1 x 3.38 | 0.0884 | 23.62 | 61 | 946 | 775
ROOK / AW | 636 | 322 | 644 | 326 | 24 x 4.14 | 7 x 2.76 | 0.0859 | 24.82 | 98 | 1168 | 777
GROSBEAK / AW | 636 | 322 | 646.1 | 327 | 26 x 3.97 | 7 x 3.09 | 0.0853 | 25.15 | 110 | 1238 | 783
SOOTER / AW | 636 | 322 | 650.5 | 330 | 30 x 3.7 | 7 x 3.7 | 0.0834 | 25.88 | 130 | 1391 | 798
EGRET / AW | 636 | 322 | 650.2 | 329 | 30 x 3.7 | 19 x 2.22 | 0.0835 | 25.88 | 133 | 1381 | 798
FLAMINGO / AW | 666.6 | 338 | 675.4 | 342 | 24 x 4.23 | 7 x 2.82 | 0.0823 | 25.4 | 103 | 1225 | 799
GANNET / AW | 666.6 | 338 | 676.6 | 343 | 26 x 4.07 | 7 x 3.16 | 0.0812 | 25.76 | 116 | 1298 | 807
STILT / AW | 715.5 | 363 | 725 | 367 | 24 x 4.39 | 7 x 2.92 | 0.0764 | 26.31 | 110 | 1314 | 837
STARLING / AW | 715.5 | 363 | 727.4 | 369 | 26 x 4.21 | 7 x 3.28 | 0.0758 | 26.7 | 122 | 1393 | 844
REDWING / AW | 715.5 | 363 | 730.9 | 370 | 30 x 3.92 | 19 x 2.35 | 0.0744 | 27.46 | 149 | 1552 | 859
COOT / AW | 795 | 403 | 797.2 | 404 | 36 x 3.77 | 1 x 3.77 | 0.0711 | 26.42 | 74 | 1183 | 868
CUCKOO / AW | 795 | 403 | 805 | 408 | 24 x 4.62 | 7 x 3.08 | 0.069 | 27.74 | 122 | 1460 | 894
DRAKE / AW | 795 | 403 | 807.6 | 409 | 26 x 4.44 | 7 x 3.45 | 0.0682 | 28.14 | 136 | 1549 | 903
TERN / AW | 795 | 403 | 800.4 | 406 | 45 x 3.38 | 7 x 2.25 | 0.0701 | 27 | 96 | 1298 | 880
CONDOR / AW | 795 | 403 | 805 | 408 | 54 x 3.08 | 7 x 3.08 | 0.069 | 27.74 | 124 | 1458 | 894
MALLARY / AW | 795 | 403 | 812.7 | 412 | 30 x 4.14 | 19 x 2.48 | 0.0667 | 28.96 | 165 | 1726 | 921
RUDDY / AW | 795 | 403 | 906.1 | 459 | 45 x 3.59 | 7 x 2.4 | 0.0621 | 28.73 | 107 | 1470 | 951
CANARY / AW | 900 | 456 | 911.4 | 462 | 54 x 3.28 | 7 x 3.28 | 0.0608 | 29.51 | 138 | 1653 | 969
CATBIRD / AW | 900 | 456 | 956.6 | 485 | 36 x 4.14 | 1 x 4.14 | 0.0589 | 28.96 | 87 | 1420 | 978
RAIL / AW | 954 | 483 | 960.4 | 487 | 45 x 3.7 | 7 x 2.47 | 0.0585 | 29.59 | 113 | 1558 | 988
CARDINAL / AW | 954 | 483 | 966.1 | 490 | 54 x 3.38 | 7 x 3.38 | 0.0573 | 30.38 | 146 | 1752 | 1006
TANAGER / AW | 1033.5 | 524 | 1035.8 | 525 | 36 x 4.3 | 1 x 4.3 | 0.0546 | 30.12 | 94 | 1537 | 1027
ORTOLAN / AW | 1033.5 | 524 | 1040 | 527 | 45 x 3.85 | 7 x 2.57 | 0.054 | 30.78 | 121 | 1688 | 1039
CURLEW / AW | 1033.5 | 524 | 1046.1 | 530 | 54 x 3.51 | 7 x 3.51 | 0.0531 | 31.62 | 158 | 1896 | 1056
BLUEJAY / AW | 1113 | 564 | 1120.5 | 568 | 45 x 4 | 7 x 2.66 | 0.0501 | 31.98 | 130 | 1819 | 1090
FINCH / AW | 1113 | 564 | 1127.8 | 571 | 54 x 3.65 | 19 x 2.19 | 0.0494 | 32.84 | 167 | 2043 | 1106
BUNTING / AW | 1192.5 | 604 | 1201 | 609 | 45 x 4.14 | 7 x 2.76 | 0.0467 | 33.07 | 139 | 1948 | 1138
GRACKLE / AW | 1192.5 | 604 | 1206.7 | 611 | 54 x 3.77 | 19 x 2.27 | 0.0463 | 33.99 | 179 | 2188 | 1152
SKYLARK / AW | 1272 | 645 | 1275.4 | 646 | 36 x 4.78 | 1 x 4.78 | 0.0442 | 33.43 | 114 | 1893 | 1172
BITTERN / AW | 1272 | 645 | 1280.6 | 649 | 45 x 4.27 | 7 x 2.85 | 0.0439 | 34.16 | 149 | 2078 | 1184
PHEASANT / AW | 1272 | 645 | 1287.7 | 652 | 54 x 3.9 | 19 x 2.34 | 0.0433 | 35.1 | 189 | 2333 | 1201
DIPPER / AW | 1351.5 | 685 | 1360.1 | 689 | 45 x 4.4 | 7 x 2.93 | 0.0414 | 35.2 | 158 | 2207 | 1228
MARTIN / AW | 1351.5 | 685 | 1367.7 | 693 | 54 x 4.02 | 19 x 2.41 | 0.0407 | 36.17 | 201 | 2478 | 1248
BOBOLINK / AW | 1431 | 725 | 1440.2 | 730 | 45 x 4.53 | 7 x 3.02 | 0.039 | 36.25 | 167 | 2336 | 1274
PLOVER / AW | 1431 | 725 | 1448.9 | 734 | 54 x 4.14 | 19 x 2.48 | 0.0384 | 37.21 | 212 | 2625 | 1294
NUTHATCH / AW | 1510.5 | 765 | 1520.5 | 770 | 45 x 4.65 | 7 x 3.1 | 0.037 | 37.24 | 177 | 2467 | 1317
PARROT / AW | 1510.5 | 765 | 1528.2 | 774 | 54 x 4.25 | 19 x 2.55 | 0.0364 | 38.23 | 224 | 2768 | 1337
LAPWING / AW | 1590 | 806 | 1601.2 | 811 | 45 x 4.78 | 7 x 3.18 | 0.0351 | 38.2 | 186 | 2598 | 1360
FALCON / AW | 1590 | 806 | 1609.8 | 816 | 54 x 4.36 | 19 x 2.62 | 0.0346 | 39.24 | 236 | 2917 | 1380
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values based on Aluminum clad steel (normal strength), different type of Aluminum clad steel core are also according to customer request as per ASTM B 502
** ACSR / AW with High Strength Steel Wires
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 35 °C , final temperature of 80 °C, wind velocity of 0.6 m/sec, solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## ACSR-AW IEC 61089
Aluminum Conductor Aluminum Clad Steel Reinforced (ACSR / AW)
Product-code | Total Cross | Number and Nominal |  | Max. D.C. Conductor | Approx. Overall | Calculated | Approx. | Rated
| Sectional Area | Diameter of Wires |  | Resistance at 20 oC | Diameter | Breaking Load | Weight | Current
| mm2 | Aluminum No. x mm | Aluminum Clad Steel No. x mm | Ω/km | mm | KN | Kg/km | Amps
B - IEC 61089 (A1/SA1A)
A1/SA1A - 16 | 17.9 | 6 x 1.81 | 1 x 1.81 | 1.7923 | 5.43 | 5.91 | 59 | 148
A1/SA1A - 25 | 28 | 6 x 2.26 | 1 x 2.26 | 1.1471 | 6.78 | 9 | 92.1 | 197
A1/SA1A - 40 | 44.8 | 6 x 2.85 | 1 x 2.85 | 0.7169 | 8.55 | 14.21 | 147.4 | 265
A1/SA1A - 63 | 70.6 | 6 x 3.58 | 1 x 3.58 | 0.4552 | 10.7 | 21.17 | 232.2 | 355
A1/SA1A - 100 | 112 | 6 x 4.51 | 1 x 4.51 | 0.2868 | 13.5 | 31.84 | 368.6 | 478
A1/SA1A - 125 | 130 | 18 x 2.95 | 1 x 2.95 | 0.2304 | 14.8 | 29.18 | 384.3 | 548
A1/SA1A - 125 | 140 | 26 x 2.43 | 7 x 1.89 | 0.2308 | 15.4 | 44.49 | 460.8 | 554
A1/SA1A - 160 | 167 | 18 x 3.34 | 1 x 3.34 | 0.18 | 16.7 | 36.38 | 491.9 | 642
A1/SA1A - 160 | 179 | 26 x 2.74 | 7 x 2.13 | 0.1803 | 17.4 | 56.18 | 589.8 | 649
A1/SA1A - 200 | 208 | 18 x 3.74 | 1 x 3.74 | 0.144 | 18.7 | 43.62 | 614.9 | 741
A1/SA1A - 200 | 223 | 26 x 3.07 | 7 x 2.39 | 0.1443 | 19.4 | 69.27 | 737.2 | 749
A1/SA1A - 250 | 268 | 22 x 3.76 | 7 x 2.09 | 0.1153 | 21.3 | 67.8 | 830.9 | 861
A1/SA1A - 250 | 279 | 26 x 3.43 | 7 x 2.67 | 0.1154 | 21.7 | 86.58 | 921.5 | 865
A1/SA1A - 315 | 331 | 45 x 2.96 | 7 x 1.97 | 0.0917 | 23.7 | 78.33 | 996.4 | 995
A1/SA1A - 315 | 352 | 26 x 3.85 | 7 x 2.99 | 0.0916 | 24.4 | 107.58 | 1161.1 | 1004
A1/SA1A - 400 | 420 | 45 x 3.34 | 7 x 2.22 | 0.0722 | 26.7 | 97.5 | 1265.3 | 1160
A1/SA1A - 400 | 438 | 54 x 3.02 | 7 x 3.02 | 0.0723 | 27.2 | 124.2 | 1402.9 | 1166
A1/SA1A - 450 | 473 | 45 x 3.54 | 7 x 2.36 | 0.0642 | 28.3 | 107.48 | 1423.4 | 1250
A1/SA1A - 450 | 492 | 54 x 3.21 | 7 x 3.21 | 0.0642 | 28.9 | 139.72 | 1578.2 | 1258
A1/SA1A - 500 | 525 | 45 x 3.73 | 7 x 2.49 | 0.0578 | 29.8 | 119.42 | 1581.6 | 1336
A1/SA1A - 500 | 547 | 54 x 3.38 | 7 x 3.38 | 0.0578 | 30.4 | 153.99 | 1753.6 | 1344
A1/SA1A - 560 | 589 | 45 x 3.95 | 7 x 2.63 | 0.0516 | 31.6 | 133.75 | 1771.4 | 1437
A1/SA1A - 560 | 612 | 54 x 3.58 | 19 x 2.15 | 0.0516 | 32.2 | 169.36 | 1956.3 | 1445
A1/SA1A - 630 | 662 | 45 x 4.19 | 7 x 2.79 | 0.0458 | 33.5 | 150.47 | 1992.8 | 1548
A1/SA1A - 630 | 688 | 54 x 3.79 | 19 x 2.28 | 0.0459 | 34.2 | 190.52 | 2200.9 | 1557
A1/SA1A - 710 | 746 | 45 x 4.44 | 7 x 2.96 | 0.0407 | 35.6 | 169.57 | 2245.8 | 1668
A1/SA1A - 710 | 775 | 54 x 4.03 | 19 x 2.42 | 0.0407 | 36.3 | 214.72 | 2480.3 | 1678
A1/SA1A - 800 | 874 | 54 x 4.28 | 19 x 2.57 | 0.0361 | 38.5 | 241.94 | 2794.7 | 1807
The above data is approximate and subjected to manufacturing tolerance.
Note:
The above values based on Aluminum clad steel 20SA-Type A (regular tesnile strength), different type of Aluminum clad steel core are also according to customer request as per IEC 61232
The above values of current carrying capacity are calculated due to frequency up to 60 Hz, assuming an ambient temperature of 20 °C , final temperature of 80 °C, wind velocity of 1.0 m/sec. solar radiation of 900 W/m2, emissivity coefficient of 0.6, solar radiation absorption coefficient of 0.5

## AACSR-France
Aluminum Allloy Conductor Steel Reinforced (AACSR)
(a) Description:-
* An outer layer of Aluminum Alloy conductor concentrically stranded over the central core of galvanized solid or stranded steel wires to form Aluminum Alloy steel reinforced conductor.
(b) Application:-
* AACSR conductors are widely used for electrical power transmission over long distance (as an earthing Conductor). It could be used as a messenger for supporting overhead electrical cables.
(c) Technical Data:-
| Relevent Standard |  | BS EN 50182
| Conductor |  | Aluminum Alloy over the central core of galvanized solid or stranded steel wires
| Minimum bending Radius |  | 10 x outer diameter
| Packing Condition |  | Our standard length on Wooden Drum / or according to customer request
Product-code | Total Cross | Number and Nominal |  | Max. D.C. Conductor | Approx. Overall | Minimum | Approx.
| Sectional Area | Diameter of Wires |  | Resistance at 20 oC | Diameter | Breaking Load | Weight
| mm2 | Aluminum No. x mm | Steel No. x mm | Ω/km | mm | KN | Kg/km
A - BS EN 50182 (France)
PHLOX 37.7 | 37.7 | 9 x 2 | 3 x 2 | 1.175 | 8.3 | 22.86 | 151.4
PHLOX 59.7 | 59.7 | 12 x 2 | 7 x 2 | 0.8835 | 10 | 44.14 | 276
PHLOX 75.5 | 75.5 | 12 x 2.25 | 7 x 2.25 | 0.6981 | 11.3 | 55.86 | 349.3
PHLOX 94.1 | 94.1 | 15 x 2.1 | 19 x 1.38 | 0.6435 | 12.6 | 77.96 | 474.2
PHLOX 116.2 | 116.2 | 18 x 2 | 19 x 2 | 0.5921 | 14 | 104.93 | 625
PHLOX 147.1 | 147.1 | 18 x 2.25 | 19 x 2.25 | 0.4678 | 15.8 | 132.8 | 791
PASTEL 147.1 | 147.1 | 30 x 2.25 | 7 x 2.25 | 0.2795 | 15.8 | 79.12 | 547
PHLOX 181.6 | 181.6 | 18 x 2.50 | 19 x 2.50 | 0.3789 | 17.5 | 160.22 | 976.6
PASTEL 181.6 | 181.6 | 30 x 2.50 | 7 x 2.50 | 0.2264 | 17.5 | 96.31 | 675.3
PHLOX 228 | 227.8 | 18 x 2.80 | 19 x 2.80 | 0.3021 | 19.6 | 200.98 | 1225
PASTEL 228 | 227.8 | 30 x 2.80 | 7 x 2.80 | 0.1805 | 19.6 | 120.81 | 847.1
PHLOX 228 | 288.3 | 18 x 3.15 | 19 x 3.15 | 0.2387 | 22.1 | 249.93 | 1550.4
PASTEL 228 | 288.3 | 30 x 3.15 | 7 x 3.15 | 0.1426 | 22.1 | 151.26 | 1072.1
PASTEL 299 | 299.4 | 42 x 2.5 | 19 x 2.50 | 0.1622 | 22.5 | 198.51 | 1302.8
PHLOX 376 | 375.6 | 24 x 2.80 | 37 x 2.80 | 0.227 | 25.2 | 369.27 | 2202.4
PASTEL 412 | 411.7 | 32 x 3.60 | 19 x 2.40 | 0.1025 | 26.4 | 223.8 | 1571.1
POLYGONUM 1185 | 1184 | 54 x 2.80 | 37 x 2.80 | 0.0349 | 42 | 632.15 | 4430.7
The above data is approximate and subjected to manufacturing tolerance.

## ABCnew
Areal Bundled Cables (ABC):
(a)Voltage Grade
600 / 1000 VOLTS
(b) Description:-
* This type of cables are made from Aluminum Conductor (H14) insulated by Weather-Resistant XLPE +2.5% Carbon Black insulation for single core
and for multi cores, the insulated phases are assambled together with one neutral (messenger) of All Aluminum Conductors (H14),
Aluminum-Alloy Conductors (AAAC), Aluminum Conductors, Steel-Reinforced (ACSR), or Aluminum Conductors, Aluminum-Clad Steel
Reinforced (ACSR/AW). The neutral conductor may be bare or covered with an extruded Weather-Resistant XLPE + 2.5% Carbon Black insulation
(c) Application:-
* They are used for secondary over head lines on poles or as feeders to Residential premises.
The use of these cables is limited to circuits, not exceeding 600 volts phase-to-phase to a normal temperature rating of the service conductor temperature of 90 °C.
(d) Technical Data:-
| Relevent Standard |  | DIN 48201-5/6, BS EN 50182, IEC 61089, IEC 60228, IEC 60502-1, ICEA S 66-524
NFC 33-209 is also available or any other specification according to customer request
| Conductor |  | Plain hard drawn Aluminum - H14
| Insulation |  | Extruded XLPE Compound + 2.5 % Carbon Black Rated 90 oC
| Assembly (in case of more than one phase) |  | The insulated Cores are assembled together with suitable lay length.
| Minimum bending Radius |  | 10 x outer diameter
| Packing Condition |  | Our standard length on Wooden Drum / or according to customer request
(e )Note:- | 1) Extruded High Density Polyethyelene (HDPE) rated 90 oC or Low Linear Density Polyethyelene (LLDPE) rated 90 oC or PVC Compound + 2.5 % Carbon Black
Rated 70 oC or 85 oC are also available according to customer request
2) Areal Bundled cables have many options in terms of:
i) the number of phase conductors used,
ii) the type of neutral (messenger) conductor if Aluminum - H14 (equally supported), or Aluminum Alloy, Aluminum Conductors Steel-Reinforced (ACSR),
Aluminum Conductors Aluminum-Clad Steel-Reinforced (ACSR/AW) (self supported) and either it is bare or insulated,
iii) the insulation type & the phase identification.
3) This catalogue covers the design and construction as per the following:
| i) One Core Cable of: | Aluminum Conductor (H14), insulated with XLPE+2.5 C.B.%.
| ii) Duplex (Two) cores cables of: | One phase of Aluminum Conductor (H14), insulated with XLPE+2.5 C.B.%., assembled with One neutral of Aluminum Conductors (H14),
insulated with XLPE+2.5 C.B.%., identified with phase No.1 with one ridge & phase No.2 without ridges
| iii) Triplex (Three cores) cables of | Two phases of Aluminum Conductor (H14), insulated with XLPE+2.5 C.B.%., assembled with One neutral of Aluminum Conductors (H14),
insulated with XLPE+2.5 C.B.%., identified with phase No.1 with one ridge, phase No.2 with two ridges & phase No. 3 without ridges
| iv) Quadruplex (four cores) cables | Three phases of Aluminum Conductor (H14), insulated with XLPE+2.5 C.B.%., assembled with One neutral of Aluminum Conductors (H14),
insulated with XLPE+2.5 C.B.%., identified with phase No.1 with one ridge, phase No.2 with two ridges, phase No. 3 with three ridges
and Phase No. 4 without ridges
However, we can provide any other type or design or construction according to customer request
Product-code | Phase |  |  | Approx. Overall | Approx.
| Total Cross | Insulation | Max. D.C. Conductor
| Sectional Area | Thickness | Resistance at 20 oC | Diameter | Weight
| mm2 | mm | Ω/km | mm | Kg/km
A) One Core
PA-BT11-W3-01-U0 | 16 | 0.7 | 1.91 | 3.5 | 60
PA-BT12-W3-01-U0 | 25 | 0.9 | 1.2 | 8.1 | 95
PA-BT13-W3-01-U0 | 35 | 0.9 | 0.868 | 9.3 | 130
PA-BT14-W3-01-U0 | 50 | 1 | 0.641 | 11 | 180
PA-BT15-W3-01-U0 | 70 | 1.1 | 0.443 | 12.7 | 230
PA-BT16-W3-01-U0 | 95 | 1.1 | 0.32 | 14.7 | 320
PA-BT17-W3-01-U0 | 120 | 1.2 | 0.253 | 16.4 | 395
B) Two Cores (Duplex)
PA-BT11-W3-02-U0 | 16 | 1.2 | 1.91 | 15 | 145
PA-BT12-W3-02-U0 | 25 | 1.2 | 1.2 | 17.4 | 205
PA-BT13-W3-02-U0 | 35 | 1.2 | 0.868 | 19.8 | 275
PA-BT14-W3-02-U0 | 50 | 1.5 | 0.641 | 24 | 400
PA-BT15-W3-02-U0 | 70 | 1.5 | 0.443 | 27 | 500
PA-BT16-W3-02-U0 | 95 | 1.5 | 0.32 | 31 | 675
PA-BT17-W3-02-U0 | 120 | 1.7 | 0.253 | 34.8 | 850
C) Three Cores (Triplex)
PA-BT11-W3-03-U0 | 16 | 1.2 | 1.91 | 16.2 | 220
PA-BT12-W3-03-U0 | 25 | 1.2 | 1.2 | 18.8 | 305
PA-BT13-W3-03-U0 | 35 | 1.2 | 0.868 | 21.4 | 410
PA-BT14-W3-03-U0 | 50 | 1.5 | 0.641 | 25.9 | 600
PA-BT15-W3-03-U0 | 70 | 1.5 | 0.443 | 29.2 | 745
PA-BT16-W3-03-U0 | 95 | 1.5 | 0.32 | 33.5 | 1015
PA-BT17-W3-03-U0 | 120 | 1.7 | 0.253 | 37.6 | 1275
D) Four Cores (Quadruplex)
PA-BT11-W3-01-U0 | 16 | 1.2 | 1.91 | 18.2 | 290
PA-BT12-W3-04-U0 | 25 | 1.2 | 1.2 | 21.1 | 410
PA-BT13-W3-04-U0 | 35 | 1.2 | 0.868 | 24 | 550
PA-BT14-W3-04-U0 | 50 | 1.5 | 0.641 | 29 | 800
PA-BT15-W3-04-U0 | 70 | 1.5 | 0.443 | 32.7 | 995
PA-BT16-W3-04-U0 | 95 | 1.5 | 0.32 | 37.5 | 1355
PA-BT17-W3-04-U0 | 120 | 1.7 | 0.253 | 42.1 | 1700
The above data is approximate and subjected to manufacturing tolerance.